## Key
DMU TRT data:
The purpose of this data is to estimate effective thermal properties of the DMU BHE arrangement and could be used with DMU BHE operational data-set.The data includes flow and return temperature of the ground loop circulating fluid for the duration of the test. The TRT data supplied by the contractor had unsettled temperature fluctuations for the first 66 minutes. So, the data have been removed and presented here.
The borehole parameters and estimated thermal properties are provided in seperate sheets of this workbook.
For more details, Please refer
SS Naicker (2015) Performance Analysis of a Large-scale Ground Source Heat Pump System. (PhD Thesis). De Montfort University,UK. [online]. Available from: https://www.dora.dmu.ac.uk

## TRT data
Minutes | T flow (°C) | T return (°C)
1 | 13.237 | 12.669
2 | 13.203 | 12.709
3 | 13.267 | 16.169
4 | 13.49 | 16.228
5 | 13.704 | 16.556
6 | 17.449 | 18.221
7 | 18.248 | 18.473
8 | 18.663 | 18.894
9 | 19.162 | 19.137
10 | 19.197 | 19.055
11 | 19.18 | 19.057
12 | 19.238 | 19.091
13 | 19.279 | 19.133
14 | 19.35 | 19.211
15 | 19.402 | 19.266
16 | 19.454 | 19.32
17 | 19.49 | 19.351
18 | 19.533 | 19.403
19 | 24.826 | 19.466
20 | 28.011 | 19.531
21 | 29.774 | 19.563
22 | 33.356 | 19.617
23 | 34.335 | 19.713
24 | 34.337 | 19.81
25 | 34.07 | 19.9
26 | 33.263 | 19.983
27 | 30.755 | 20.047
28 | 28.98 | 20.05
29 | 28.765 | 20.042
30 | 28.669 | 20.044
31 | 28.465 | 20.06
32 | 28.476 | 20.073
33 | 28.554 | 20.167
34 | 28.7 | 20.471
35 | 28.896 | 20.783
36 | 29.332 | 21.215
37 | 30.399 | 21.647
38 | 34.148 | 21.891
39 | 35.792 | 22.02
40 | 36.865 | 22.064
41 | 36.904 | 22.07
42 | 36.477 | 22.086
43 | 35.502 | 22.107
44 | 33.007 | 22.129
45 | 31.51 | 22.125
46 | 30.933 | 22.11
47 | 30.597 | 22.107
48 | 30.524 | 22.125
49 | 30.746 | 22.167
50 | 31.19 | 22.232
51 | 31.762 | 22.308
52 | 31.883 | 22.427
53 | 31.751 | 22.675
54 | 32.189 | 22.977
55 | 33.065 | 23.231
56 | 33.737 | 23.385
57 | 34.142 | 23.421
58 | 34.079 | 23.392
59 | 33.974 | 23.366
60 | 33.806 | 23.346
61 | 33.53 | 23.332
62 | 33.215 | 23.323
63 | 33.088 | 23.328
64 | 33 | 23.355
65 | 33.279 | 23.395
66 | 33.239 | 23.44
67 | 33.057 | 23.478
68 | 33.103 | 23.529
69 | 33.315 | 23.6
70 | 33.464 | 23.69
71 | 34.818 | 23.771
72 | 35.293 | 23.835
73 | 35.197 | 23.883
74 | 35.047 | 23.927
75 | 35.012 | 23.96
76 | 34.882 | 23.975
77 | 34.77 | 23.98
78 | 34.7 | 23.99
79 | 34.57 | 23.998
80 | 34.424 | 24.014
81 | 34.439 | 24.031
82 | 34.715 | 24.044
83 | 34.9 | 24.06
84 | 34.806 | 24.079
85 | 34.822 | 24.105
86 | 35.029 | 24.148
87 | 34.707 | 24.219
88 | 34.813 | 24.279
89 | 35.111 | 24.326
90 | 34.937 | 24.365
91 | 34.949 | 24.404
92 | 35.109 | 24.435
93 | 34.985 | 24.463
94 | 34.979 | 24.488
95 | 34.97 | 24.51
96 | 34.949 | 24.531
97 | 34.953 | 24.563
98 | 35.047 | 24.597
99 | 35.197 | 24.629
100 | 35.355 | 24.661
101 | 35.469 | 24.688
102 | 35.517 | 24.707
103 | 35.551 | 24.731
104 | 35.625 | 24.761
105 | 35.67 | 24.78
106 | 35.668 | 24.798
107 | 35.637 | 24.817
108 | 35.598 | 24.833
109 | 35.597 | 24.85
110 | 35.61 | 24.868
111 | 35.629 | 24.882
112 | 35.653 | 24.895
113 | 35.623 | 24.91
114 | 35.687 | 24.932
115 | 35.706 | 24.958
116 | 35.736 | 24.98
117 | 35.726 | 25.004
118 | 35.736 | 25.032
119 | 35.749 | 25.06
120 | 35.785 | 25.084
121 | 35.825 | 25.109
122 | 35.851 | 25.129
123 | 35.908 | 25.15
124 | 35.933 | 25.168
125 | 36.012 | 25.186
126 | 36.139 | 25.204
127 | 36.189 | 25.221
128 | 36.265 | 25.237
129 | 36.298 | 25.251
130 | 36.295 | 25.265
131 | 36.292 | 25.28
132 | 36.298 | 25.293
133 | 36.304 | 25.302
134 | 36.302 | 25.317
135 | 36.289 | 25.325
136 | 36.265 | 25.338
137 | 36.214 | 25.35
138 | 36.169 | 25.367
139 | 36.214 | 25.381
140 | 36.269 | 25.396
141 | 36.323 | 25.413
142 | 36.315 | 25.434
143 | 36.358 | 25.456
144 | 36.392 | 25.476
145 | 36.424 | 25.496
146 | 36.471 | 25.513
147 | 36.513 | 25.531
148 | 36.555 | 25.548
149 | 36.643 | 25.558
150 | 36.605 | 25.573
151 | 36.628 | 25.585
152 | 36.664 | 25.595
153 | 36.693 | 25.604
154 | 36.719 | 25.615
155 | 36.723 | 25.621
156 | 36.734 | 25.632
157 | 36.763 | 25.643
158 | 36.783 | 25.654
159 | 36.833 | 25.662
160 | 36.847 | 25.674
161 | 36.858 | 25.683
162 | 36.856 | 25.693
163 | 36.87 | 25.706
164 | 36.898 | 25.716
165 | 36.898 | 25.731
166 | 36.914 | 25.742
167 | 36.962 | 25.752
168 | 36.972 | 25.764
169 | 37.101 | 25.774
170 | 37.016 | 25.786
171 | 36.995 | 25.796
172 | 37.043 | 25.808
173 | 37.064 | 25.815
174 | 37.082 | 25.826
175 | 37.094 | 25.837
176 | 37.12 | 25.848
177 | 37.124 | 25.858
178 | 37.139 | 25.866
179 | 37.13 | 25.877
180 | 37.15 | 25.887
181 | 37.175 | 25.896
182 | 37.192 | 25.902
183 | 37.224 | 25.913
184 | 37.258 | 25.926
185 | 37.266 | 25.938
186 | 37.283 | 25.949
187 | 37.331 | 25.956
188 | 37.364 | 25.965
189 | 37.379 | 25.974
190 | 37.373 | 25.98
191 | 37.374 | 25.988
192 | 37.383 | 25.997
193 | 37.396 | 26.004
194 | 37.4 | 26.013
195 | 37.425 | 26.021
196 | 37.434 | 26.029
197 | 37.464 | 26.037
198 | 37.467 | 26.045
199 | 37.487 | 26.054
200 | 37.481 | 26.06
201 | 37.476 | 26.07
202 | 37.491 | 26.079
203 | 37.47 | 26.085
204 | 37.477 | 26.093
205 | 37.493 | 26.104
206 | 37.505 | 26.115
207 | 37.51 | 26.123
208 | 37.53 | 26.134
209 | 37.565 | 26.141
210 | 37.575 | 26.15
211 | 37.583 | 26.159
212 | 37.598 | 26.168
213 | 37.634 | 26.176
214 | 37.655 | 26.183
215 | 37.673 | 26.194
216 | 37.693 | 26.201
217 | 37.713 | 26.204
218 | 37.725 | 26.208
219 | 37.742 | 26.216
220 | 37.759 | 26.225
221 | 37.796 | 26.232
222 | 37.812 | 26.236
223 | 37.82 | 26.242
224 | 37.852 | 26.246
225 | 37.865 | 26.254
226 | 37.886 | 26.26
227 | 37.901 | 26.264
228 | 38.112 | 26.266
229 | 38.179 | 26.272
230 | 38.223 | 26.275
231 | 38.24 | 26.28
232 | 38.256 | 26.285
233 | 38.283 | 26.285
234 | 38.308 | 26.291
235 | 38.339 | 26.29
236 | 38.285 | 26.292
237 | 37.985 | 26.295
238 | 37.989 | 26.299
239 | 38.004 | 26.302
240 | 38.014 | 26.306
241 | 38.012 | 26.307
242 | 38.016 | 26.315
243 | 38.022 | 26.322
244 | 38.035 | 26.332
245 | 38.041 | 26.341
246 | 38.066 | 26.352
247 | 38.076 | 26.364
248 | 38.099 | 26.379
249 | 38.14 | 26.391
250 | 38.142 | 26.4
251 | 38.157 | 26.41
252 | 38.166 | 26.423
253 | 38.184 | 26.426
254 | 38.198 | 26.427
255 | 38.201 | 26.432
256 | 38.222 | 26.438
257 | 38.242 | 26.444
258 | 38.247 | 26.447
259 | 38.264 | 26.455
260 | 38.274 | 26.457
261 | 38.288 | 26.463
262 | 38.292 | 26.466
263 | 38.299 | 26.47
264 | 38.311 | 26.475
265 | 38.303 | 26.48
266 | 38.304 | 26.485
267 | 38.317 | 26.49
268 | 38.306 | 26.492
269 | 38.317 | 26.501
270 | 38.317 | 26.507
271 | 38.331 | 26.512
272 | 38.339 | 26.519
273 | 38.334 | 26.524
274 | 38.331 | 26.533
275 | 38.331 | 26.539
276 | 38.343 | 26.542
277 | 38.354 | 26.548
278 | 38.359 | 26.556
279 | 38.378 | 26.564
280 | 38.371 | 26.568
281 | 38.377 | 26.573
282 | 38.386 | 26.58
283 | 38.399 | 26.583
284 | 38.413 | 26.59
285 | 38.458 | 26.591
286 | 38.486 | 26.596
287 | 38.5 | 26.604
288 | 38.507 | 26.61
289 | 38.522 | 26.613
290 | 38.532 | 26.615
291 | 38.542 | 26.62
292 | 38.557 | 26.627
293 | 38.544 | 26.628
294 | 38.538 | 26.633
295 | 38.557 | 26.631
296 | 38.566 | 26.638
297 | 38.577 | 26.643
298 | 38.577 | 26.648
299 | 38.56 | 26.651
300 | 38.566 | 26.653
301 | 38.578 | 26.655
302 | 38.581 | 26.658
303 | 38.583 | 26.664
304 | 38.551 | 26.669
305 | 38.559 | 26.673
306 | 38.568 | 26.68
307 | 38.57 | 26.685
308 | 38.587 | 26.693
309 | 38.584 | 26.697
310 | 38.586 | 26.701
311 | 38.581 | 26.704
312 | 38.591 | 26.706
313 | 38.603 | 26.712
314 | 38.594 | 26.719
315 | 38.596 | 26.726
316 | 38.614 | 26.733
317 | 38.625 | 26.737
318 | 38.62 | 26.743
319 | 38.621 | 26.749
320 | 38.609 | 26.752
321 | 38.639 | 26.758
322 | 38.637 | 26.759
323 | 38.656 | 26.76
324 | 38.67 | 26.768
325 | 38.679 | 26.773
326 | 38.68 | 26.78
327 | 38.692 | 26.783
328 | 38.689 | 26.785
329 | 38.712 | 26.785
330 | 38.704 | 26.789
331 | 38.712 | 26.798
332 | 38.716 | 26.801
333 | 38.718 | 26.803
334 | 38.743 | 26.806
335 | 38.76 | 26.808
336 | 38.77 | 26.81
337 | 38.769 | 26.813
338 | 38.768 | 26.815
339 | 38.84 | 26.821
340 | 38.899 | 26.822
341 | 38.913 | 26.827
342 | 38.941 | 26.829
343 | 38.977 | 26.831
344 | 38.99 | 26.829
345 | 38.982 | 26.831
346 | 38.991 | 26.833
347 | 39.005 | 26.834
348 | 39.024 | 26.839
349 | 39.019 | 26.841
350 | 39.03 | 26.842
351 | 39.039 | 26.841
352 | 39.057 | 26.838
353 | 39.042 | 26.836
354 | 39.048 | 26.838
355 | 39.061 | 26.84
356 | 39.057 | 26.838
357 | 39.059 | 26.841
358 | 39.231 | 26.846
359 | 39.208 | 26.849
360 | 39.228 | 26.856
361 | 39.251 | 26.861
362 | 39.257 | 26.863
363 | 39.269 | 26.867
364 | 39.273 | 26.869
365 | 39.272 | 26.87
366 | 39.285 | 26.871
367 | 39.306 | 26.873
368 | 39.321 | 26.876
369 | 39.336 | 26.875
370 | 39.342 | 26.876
371 | 39.339 | 26.877
372 | 39.345 | 26.876
373 | 39.348 | 26.877
374 | 39.358 | 26.874
375 | 39.368 | 26.876
376 | 39.371 | 26.882
377 | 39.382 | 26.886
378 | 39.383 | 26.89
379 | 39.396 | 26.893
380 | 39.396 | 26.893
381 | 39.405 | 26.897
382 | 39.411 | 26.899
383 | 39.438 | 26.896
384 | 39.437 | 26.896
385 | 39.451 | 26.903
386 | 39.459 | 26.905
387 | 39.479 | 26.91
388 | 39.5 | 26.913
389 | 39.503 | 26.906
390 | 39.504 | 26.906
391 | 39.495 | 26.915
392 | 39.48 | 26.916
393 | 39.477 | 26.918
394 | 39.482 | 26.92
395 | 39.49 | 26.925
396 | 39.493 | 26.929
397 | 39.51 | 26.933
398 | 39.504 | 26.934
399 | 39.512 | 26.935
400 | 39.523 | 26.937
401 | 39.539 | 26.942
402 | 39.546 | 26.946
403 | 39.545 | 26.95
404 | 39.538 | 26.952
405 | 39.543 | 26.956
406 | 39.569 | 26.959
407 | 39.622 | 26.959
408 | 39.575 | 26.964
409 | 39.583 | 26.964
410 | 39.582 | 26.967
411 | 39.586 | 26.968
412 | 39.595 | 26.972
413 | 39.609 | 26.974
414 | 39.618 | 26.978
415 | 39.628 | 26.983
416 | 39.637 | 26.986
417 | 39.634 | 26.99
418 | 39.641 | 26.993
419 | 39.635 | 26.994
420 | 39.641 | 26.998
421 | 39.662 | 27
422 | 39.649 | 27.002
423 | 39.668 | 27.002
424 | 39.668 | 27.005
425 | 39.679 | 27.009
426 | 39.679 | 27.011
427 | 39.685 | 27.009
428 | 39.681 | 27.014
429 | 39.686 | 27.016
430 | 39.693 | 27.019
431 | 39.702 | 27.023
432 | 39.711 | 27.026
433 | 39.715 | 27.026
434 | 39.719 | 27.029
435 | 39.726 | 27.031
436 | 39.735 | 27.034
437 | 39.74 | 27.037
438 | 39.744 | 27.04
439 | 39.751 | 27.043
440 | 39.746 | 27.045
441 | 39.758 | 27.048
442 | 39.758 | 27.052
443 | 39.777 | 27.056
444 | 39.769 | 27.057
445 | 39.783 | 27.061
446 | 39.786 | 27.063
447 | 39.783 | 27.064
448 | 39.786 | 27.065
449 | 39.775 | 27.067
450 | 39.782 | 27.072
451 | 39.789 | 27.075
452 | 39.796 | 27.079
453 | 39.795 | 27.076
454 | 39.812 | 27.076
455 | 39.81 | 27.08
456 | 39.822 | 27.087
457 | 39.82 | 27.093
458 | 39.819 | 27.092
459 | 39.827 | 27.096
460 | 39.825 | 27.098
461 | 39.837 | 27.101
462 | 39.843 | 27.106
463 | 39.847 | 27.106
464 | 39.854 | 27.106
465 | 39.953 | 27.107
466 | 39.87 | 27.109
467 | 39.861 | 27.111
468 | 39.861 | 27.111
469 | 39.899 | 27.116
470 | 39.94 | 27.119
471 | 39.92 | 27.122
472 | 39.93 | 27.127
473 | 39.927 | 27.127
474 | 39.922 | 27.129
475 | 39.93 | 27.133
476 | 39.925 | 27.13
477 | 39.929 | 27.133
478 | 39.909 | 27.133
479 | 39.908 | 27.133
480 | 39.89 | 27.139
481 | 39.884 | 27.141
482 | 39.887 | 27.144
483 | 39.886 | 27.149
484 | 39.887 | 27.151
485 | 39.877 | 27.153
486 | 39.878 | 27.157
487 | 39.873 | 27.163
488 | 39.871 | 27.166
489 | 39.87 | 27.167
490 | 39.862 | 27.169
491 | 39.867 | 27.17
492 | 39.886 | 27.174
493 | 39.868 | 27.18
494 | 39.877 | 27.183
495 | 39.877 | 27.186
496 | 39.886 | 27.191
497 | 39.886 | 27.19
498 | 39.883 | 27.194
499 | 39.899 | 27.196
500 | 39.903 | 27.205
501 | 39.912 | 27.208
502 | 39.913 | 27.21
503 | 39.913 | 27.211
504 | 39.917 | 27.213
505 | 39.916 | 27.215
506 | 39.915 | 27.22
507 | 39.936 | 27.219
508 | 39.945 | 27.22
509 | 39.943 | 27.222
510 | 39.942 | 27.226
511 | 39.936 | 27.228
512 | 39.943 | 27.23
513 | 39.95 | 27.232
514 | 39.953 | 27.235
515 | 39.961 | 27.234
516 | 39.975 | 27.238
517 | 39.988 | 27.242
518 | 39.998 | 27.243
519 | 39.996 | 27.245
520 | 40.004 | 27.246
521 | 40 | 27.249
522 | 40.011 | 27.25
523 | 40.01 | 27.254
524 | 40.089 | 27.256
525 | 40.04 | 27.256
526 | 40.031 | 27.258
527 | 40.033 | 27.257
528 | 40.046 | 27.261
529 | 40.042 | 27.261
530 | 40.05 | 27.258
531 | 40.05 | 27.26
532 | 40.057 | 27.262
533 | 40.069 | 27.266
534 | 40.078 | 27.269
535 | 40.068 | 27.272
536 | 40.063 | 27.274
537 | 40.068 | 27.276
538 | 40.071 | 27.279
539 | 40.075 | 27.279
540 | 40.084 | 27.28
541 | 40.073 | 27.283
542 | 40.076 | 27.283
543 | 40.078 | 27.286
544 | 40.08 | 27.284
545 | 40.088 | 27.286
546 | 40.083 | 27.293
547 | 40.083 | 27.294
548 | 40.094 | 27.296
549 | 40.112 | 27.298
550 | 40.154 | 27.3
551 | 40.155 | 27.303
552 | 40.143 | 27.304
553 | 40.176 | 27.309
554 | 40.186 | 27.311
555 | 40.178 | 27.312
556 | 40.12 | 27.314
557 | 40.104 | 27.313
558 | 40.11 | 27.313
559 | 40.111 | 27.317
560 | 40.122 | 27.32
561 | 40.144 | 27.322
562 | 40.152 | 27.325
563 | 40.152 | 27.327
564 | 40.154 | 27.327
565 | 40.15 | 27.33
566 | 40.149 | 27.332
567 | 40.145 | 27.335
568 | 40.163 | 27.337
569 | 40.166 | 27.339
570 | 40.173 | 27.343
571 | 40.175 | 27.344
572 | 40.127 | 27.349
573 | 40.13 | 27.351
574 | 40.126 | 27.355
575 | 40.117 | 27.354
576 | 40.124 | 27.358
577 | 40.114 | 27.358
578 | 40.122 | 27.359
579 | 40.132 | 27.361
580 | 40.149 | 27.365
581 | 40.161 | 27.365
582 | 40.261 | 27.369
583 | 40.194 | 27.372
584 | 40.159 | 27.372
585 | 40.156 | 27.376
586 | 40.168 | 27.376
587 | 40.16 | 27.376
588 | 40.184 | 27.375
589 | 40.173 | 27.376
590 | 40.174 | 27.38
591 | 40.175 | 27.382
592 | 40.175 | 27.385
593 | 40.183 | 27.385
594 | 40.189 | 27.385
595 | 40.188 | 27.387
596 | 40.186 | 27.389
597 | 40.179 | 27.392
598 | 40.175 | 27.395
599 | 40.169 | 27.399
600 | 40.173 | 27.404
601 | 40.165 | 27.406
602 | 40.172 | 27.409
603 | 40.165 | 27.411
604 | 40.16 | 27.412
605 | 40.156 | 27.413
606 | 40.139 | 27.417
607 | 40.13 | 27.416
608 | 40.135 | 27.421
609 | 40.134 | 27.423
610 | 40.147 | 27.424
611 | 40.147 | 27.429
612 | 40.147 | 27.43
613 | 40.153 | 27.435
614 | 40.153 | 27.438
615 | 40.15 | 27.44
616 | 40.152 | 27.442
617 | 40.171 | 27.444
618 | 40.169 | 27.446
619 | 40.168 | 27.448
620 | 40.177 | 27.451
621 | 40.188 | 27.455
622 | 40.189 | 27.458
623 | 40.196 | 27.458
624 | 40.196 | 27.459
625 | 40.201 | 27.46
626 | 40.214 | 27.462
627 | 40.225 | 27.462
628 | 40.224 | 27.463
629 | 40.237 | 27.461
630 | 40.246 | 27.462
631 | 40.234 | 27.462
632 | 40.235 | 27.461
633 | 40.245 | 27.465
634 | 40.251 | 27.469
635 | 40.253 | 27.469
636 | 40.264 | 27.47
637 | 40.26 | 27.471
638 | 40.259 | 27.472
639 | 40.262 | 27.474
640 | 40.275 | 27.475
641 | 40.273 | 27.477
642 | 40.278 | 27.476
643 | 40.281 | 27.478
644 | 40.279 | 27.478
645 | 40.286 | 27.483
646 | 40.286 | 27.483
647 | 40.279 | 27.484
648 | 40.273 | 27.487
649 | 40.275 | 27.489
650 | 40.282 | 27.491
651 | 40.285 | 27.492
652 | 40.288 | 27.49
653 | 40.285 | 27.494
654 | 40.296 | 27.493
655 | 40.296 | 27.499
656 | 40.301 | 27.499
657 | 40.299 | 27.501
658 | 40.294 | 27.5
659 | 40.302 | 27.503
660 | 40.3 | 27.503
661 | 40.295 | 27.505
662 | 40.307 | 27.504
663 | 40.306 | 27.505
664 | 40.317 | 27.506
665 | 40.314 | 27.508
666 | 40.323 | 27.512
667 | 40.325 | 27.512
668 | 40.326 | 27.511
669 | 40.324 | 27.515
670 | 40.334 | 27.515
671 | 40.336 | 27.516
672 | 40.332 | 27.514
673 | 40.344 | 27.519
674 | 40.343 | 27.521
675 | 40.346 | 27.518
676 | 40.345 | 27.519
677 | 40.34 | 27.523
678 | 40.354 | 27.526
679 | 40.349 | 27.527
680 | 40.359 | 27.527
681 | 40.355 | 27.522
682 | 40.359 | 27.52
683 | 40.367 | 27.521
684 | 40.373 | 27.524
685 | 40.385 | 27.528
686 | 40.388 | 27.528
687 | 40.384 | 27.531
688 | 40.38 | 27.533
689 | 40.378 | 27.535
690 | 40.377 | 27.534
691 | 40.37 | 27.532
692 | 40.374 | 27.533
693 | 40.375 | 27.535
694 | 40.386 | 27.537
695 | 40.388 | 27.539
696 | 40.397 | 27.539
697 | 40.387 | 27.543
698 | 40.397 | 27.544
699 | 40.404 | 27.542
700 | 40.395 | 27.545
701 | 40.4 | 27.546
702 | 40.401 | 27.549
703 | 40.419 | 27.548
704 | 40.411 | 27.549
705 | 40.426 | 27.548
706 | 40.418 | 27.55
707 | 40.413 | 27.553
708 | 40.425 | 27.557
709 | 40.422 | 27.556
710 | 40.422 | 27.555
711 | 40.418 | 27.559
712 | 40.413 | 27.559
713 | 40.41 | 27.557
714 | 40.412 | 27.558
715 | 40.428 | 27.558
716 | 40.431 | 27.559
717 | 40.611 | 27.561
718 | 40.527 | 27.563
719 | 40.441 | 27.567
720 | 40.436 | 27.567
721 | 40.442 | 27.571
722 | 40.446 | 27.571
723 | 40.449 | 27.57
724 | 40.445 | 27.571
725 | 40.412 | 27.571
726 | 40.408 | 27.574
727 | 40.409 | 27.578
728 | 40.416 | 27.581
729 | 40.418 | 27.579
730 | 40.418 | 27.58
731 | 40.408 | 27.58
732 | 40.411 | 27.581
733 | 40.411 | 27.581
734 | 40.415 | 27.583
735 | 40.42 | 27.59
736 | 40.42 | 27.589
737 | 40.417 | 27.588
738 | 40.416 | 27.59
739 | 40.416 | 27.593
740 | 40.411 | 27.596
741 | 40.423 | 27.596
742 | 40.428 | 27.599
743 | 40.428 | 27.595
744 | 40.43 | 27.599
745 | 40.432 | 27.599
746 | 40.442 | 27.6
747 | 40.445 | 27.601
748 | 40.439 | 27.6
749 | 40.438 | 27.605
750 | 40.444 | 27.604
751 | 40.439 | 27.606
752 | 40.446 | 27.608
753 | 40.448 | 27.605
754 | 40.449 | 27.604
755 | 40.458 | 27.606
756 | 40.459 | 27.609
757 | 40.465 | 27.61
758 | 40.463 | 27.605
759 | 40.443 | 27.605
760 | 40.457 | 27.604
761 | 40.448 | 27.603
762 | 40.449 | 27.601
763 | 40.441 | 27.604
764 | 40.46 | 27.607
765 | 40.459 | 27.608
766 | 40.465 | 27.612
767 | 40.473 | 27.615
768 | 40.478 | 27.61
769 | 40.487 | 27.61
770 | 40.478 | 27.611
771 | 40.48 | 27.61
772 | 40.492 | 27.613
773 | 40.517 | 27.613
774 | 40.532 | 27.613
775 | 40.524 | 27.612
776 | 40.53 | 27.614
777 | 40.531 | 27.606
778 | 40.516 | 27.603
779 | 40.513 | 27.6
780 | 40.526 | 27.605
781 | 40.518 | 27.603
782 | 40.523 | 27.602
783 | 40.525 | 27.601
784 | 40.528 | 27.602
785 | 40.532 | 27.608
786 | 40.544 | 27.609
787 | 40.549 | 27.611
788 | 40.555 | 27.613
789 | 40.56 | 27.61
790 | 40.566 | 27.612
791 | 40.571 | 27.616
792 | 40.574 | 27.618
793 | 40.576 | 27.615
794 | 40.57 | 27.615
795 | 40.571 | 27.616
796 | 40.582 | 27.613
797 | 40.568 | 27.607
798 | 40.578 | 27.609
799 | 40.581 | 27.613
800 | 40.551 | 27.613
801 | 40.58 | 27.613
802 | 40.847 | 27.61
803 | 40.658 | 27.61
804 | 40.59 | 27.608
805 | 40.587 | 27.614
806 | 40.593 | 27.619
807 | 40.605 | 27.618
808 | 40.599 | 27.619
809 | 40.598 | 27.622
810 | 40.597 | 27.618
811 | 40.601 | 27.614
812 | 40.597 | 27.614
813 | 40.601 | 27.613
814 | 40.601 | 27.62
815 | 40.615 | 27.624
816 | 40.626 | 27.624
817 | 40.613 | 27.619
818 | 40.612 | 27.615
819 | 40.617 | 27.62
820 | 40.63 | 27.628
821 | 40.641 | 27.634
822 | 40.64 | 27.632
823 | 40.644 | 27.624
824 | 40.639 | 27.626
825 | 40.641 | 27.626
826 | 40.643 | 27.631
827 | 40.645 | 27.63
828 | 40.647 | 27.623
829 | 40.648 | 27.626
830 | 40.652 | 27.629
831 | 40.659 | 27.636
832 | 40.667 | 27.636
833 | 40.662 | 27.635
834 | 40.667 | 27.632
835 | 40.662 | 27.637
836 | 40.675 | 27.637
837 | 40.677 | 27.644
838 | 40.689 | 27.643
839 | 40.673 | 27.639
840 | 40.682 | 27.639
841 | 40.682 | 27.633
842 | 40.691 | 27.642
843 | 40.691 | 27.64
844 | 40.697 | 27.642
845 | 40.701 | 27.645
846 | 40.711 | 27.65
847 | 40.715 | 27.651
848 | 40.716 | 27.646
849 | 40.704 | 27.65
850 | 40.706 | 27.646
851 | 40.699 | 27.642
852 | 40.7 | 27.645
853 | 40.718 | 27.65
854 | 40.725 | 27.657
855 | 40.733 | 27.66
856 | 40.72 | 27.653
857 | 40.723 | 27.655
858 | 40.719 | 27.654
859 | 40.725 | 27.655
860 | 40.728 | 27.659
861 | 40.733 | 27.663
862 | 40.728 | 27.662
863 | 40.739 | 27.667
864 | 40.738 | 27.665
865 | 40.751 | 27.666
866 | 40.751 | 27.668
867 | 40.746 | 27.67
868 | 40.75 | 27.672
869 | 40.754 | 27.673
870 | 40.763 | 27.673
871 | 40.808 | 27.673
872 | 40.769 | 27.674
873 | 40.762 | 27.673
874 | 40.762 | 27.675
875 | 40.764 | 27.676
876 | 40.759 | 27.677
877 | 40.75 | 27.676
878 | 40.747 | 27.679
879 | 40.747 | 27.678
880 | 40.748 | 27.678
881 | 40.757 | 27.682
882 | 40.766 | 27.682
883 | 40.781 | 27.682
884 | 40.774 | 27.683
885 | 40.757 | 27.683
886 | 40.755 | 27.689
887 | 40.77 | 27.694
888 | 40.772 | 27.694
889 | 40.759 | 27.697
890 | 40.772 | 27.698
891 | 40.771 | 27.7
892 | 40.773 | 27.702
893 | 40.773 | 27.703
894 | 40.77 | 27.703
895 | 40.776 | 27.704
896 | 40.773 | 27.701
897 | 40.774 | 27.704
898 | 40.774 | 27.709
899 | 40.781 | 27.71
900 | 40.771 | 27.709
901 | 40.775 | 27.707
902 | 40.774 | 27.706
903 | 40.779 | 27.71
904 | 40.777 | 27.707
905 | 40.769 | 27.711
906 | 40.785 | 27.716
907 | 40.791 | 27.719
908 | 40.79 | 27.723
909 | 40.789 | 27.723
910 | 40.779 | 27.718
911 | 40.779 | 27.72
912 | 40.778 | 27.722
913 | 40.784 | 27.726
914 | 40.791 | 27.722
915 | 40.78 | 27.719
916 | 40.781 | 27.718
917 | 40.786 | 27.721
918 | 40.788 | 27.725
919 | 40.783 | 27.723
920 | 40.787 | 27.73
921 | 40.78 | 27.731
922 | 40.793 | 27.733
923 | 40.786 | 27.731
924 | 40.785 | 27.728
925 | 40.901 | 27.727
926 | 40.928 | 27.728
927 | 40.819 | 27.732
928 | 40.809 | 27.735
929 | 40.81 | 27.734
930 | 40.818 | 27.729
931 | 40.82 | 27.731
932 | 40.818 | 27.727
933 | 40.816 | 27.722
934 | 40.815 | 27.723
935 | 40.814 | 27.727
936 | 40.822 | 27.73
937 | 40.818 | 27.729
938 | 40.812 | 27.727
939 | 40.816 | 27.731
940 | 40.818 | 27.736
941 | 40.812 | 27.732
942 | 40.817 | 27.738
943 | 40.819 | 27.736
944 | 40.827 | 27.736
945 | 40.827 | 27.74
946 | 40.825 | 27.736
947 | 40.832 | 27.739
948 | 40.831 | 27.738
949 | 40.822 | 27.732
950 | 40.824 | 27.735
951 | 40.827 | 27.733
952 | 40.824 | 27.733
953 | 40.821 | 27.736
954 | 40.826 | 27.741
955 | 40.828 | 27.741
956 | 40.834 | 27.742
957 | 40.829 | 27.748
958 | 40.845 | 27.752
959 | 40.838 | 27.754
960 | 40.852 | 27.756
961 | 40.858 | 27.756
962 | 40.854 | 27.756
963 | 40.847 | 27.754
964 | 40.849 | 27.75
965 | 40.846 | 27.75
966 | 40.855 | 27.75
967 | 40.845 | 27.748
968 | 40.843 | 27.75
969 | 40.847 | 27.75
970 | 40.849 | 27.747
971 | 40.856 | 27.74
972 | 40.863 | 27.743
973 | 40.849 | 27.744
974 | 40.862 | 27.746
975 | 40.848 | 27.749
976 | 40.849 | 27.752
977 | 40.857 | 27.75
978 | 40.853 | 27.751
979 | 40.854 | 27.748
980 | 40.856 | 27.745
981 | 40.846 | 27.741
982 | 40.856 | 27.743
983 | 40.87 | 27.746
984 | 40.894 | 27.749
985 | 40.897 | 27.744
986 | 40.871 | 27.734
987 | 40.879 | 27.742
988 | 40.891 | 27.749
989 | 40.888 | 27.755
990 | 40.888 | 27.749
991 | 40.878 | 27.749
992 | 40.871 | 27.751
993 | 40.874 | 27.75
994 | 40.882 | 27.751
995 | 40.887 | 27.756
996 | 41.101 | 27.754
997 | 41.032 | 27.76
998 | 40.901 | 27.765
999 | 40.901 | 27.763
1000 | 40.891 | 27.771
1001 | 40.905 | 27.769
1002 | 40.899 | 27.768
1003 | 40.904 | 27.771
1004 | 40.91 | 27.774
1005 | 40.913 | 27.775
1006 | 40.901 | 27.77
1007 | 40.905 | 27.778
1008 | 40.914 | 27.778
1009 | 40.912 | 27.779
1010 | 40.925 | 27.779
1011 | 40.919 | 27.78
1012 | 40.938 | 27.784
1013 | 40.932 | 27.785
1014 | 40.947 | 27.788
1015 | 40.95 | 27.797
1016 | 40.965 | 27.8
1017 | 40.97 | 27.798
1018 | 40.97 | 27.797
1019 | 40.975 | 27.798
1020 | 40.983 | 27.802
1021 | 40.976 | 27.803
1022 | 40.984 | 27.803
1023 | 40.979 | 27.803
1024 | 40.98 | 27.805
1025 | 40.99 | 27.805
1026 | 40.992 | 27.807
1027 | 40.986 | 27.808
1028 | 41.001 | 27.809
1029 | 40.992 | 27.81
1030 | 40.989 | 27.81
1031 | 41 | 27.814
1032 | 40.997 | 27.816
1033 | 41.007 | 27.817
1034 | 40.997 | 27.819
1035 | 41 | 27.822
1036 | 41.004 | 27.821
1037 | 41.002 | 27.825
1038 | 41.018 | 27.828
1039 | 41.025 | 27.829
1040 | 41.026 | 27.829
1041 | 41.032 | 27.834
1042 | 41.034 | 27.833
1043 | 41.051 | 27.834
1044 | 41.043 | 27.838
1045 | 41.037 | 27.836
1046 | 41.038 | 27.836
1047 | 41.038 | 27.837
1048 | 41.045 | 27.839
1049 | 41.041 | 27.839
1050 | 41.057 | 27.836
1051 | 41.048 | 27.838
1052 | 41.049 | 27.842
1053 | 41.049 | 27.841
1054 | 41.043 | 27.845
1055 | 41.049 | 27.847
1056 | 41.056 | 27.85
1057 | 41.056 | 27.854
1058 | 41.064 | 27.856
1059 | 41.066 | 27.859
1060 | 41.067 | 27.857
1061 | 41.056 | 27.858
1062 | 41.053 | 27.861
1063 | 41.053 | 27.863
1064 | 41.061 | 27.865
1065 | 41.066 | 27.867
1066 | 41.072 | 27.872
1067 | 41.075 | 27.87
1068 | 41.07 | 27.872
1069 | 41.068 | 27.873
1070 | 41.079 | 27.875
1071 | 41.077 | 27.876
1072 | 41.08 | 27.872
1073 | 41.068 | 27.875
1074 | 41.087 | 27.878
1075 | 41.075 | 27.88
1076 | 41.218 | 27.876
1077 | 41.26 | 27.88
1078 | 41.104 | 27.884
1079 | 41.092 | 27.883
1080 | 41.09 | 27.884
1081 | 41.097 | 27.885
1082 | 41.099 | 27.889
1083 | 41.1 | 27.889
1084 | 41.095 | 27.889
1085 | 41.1 | 27.889
1086 | 41.096 | 27.885
1087 | 41.089 | 27.888
1088 | 41.091 | 27.89
1089 | 41.091 | 27.892
1090 | 41.092 | 27.891
1091 | 41.102 | 27.893
1092 | 41.1 | 27.894
1093 | 41.094 | 27.894
1094 | 41.103 | 27.898
1095 | 41.099 | 27.901
1096 | 41.103 | 27.905
1097 | 41.109 | 27.905
1098 | 41.106 | 27.903
1099 | 41.112 | 27.904
1100 | 41.112 | 27.907
1101 | 41.102 | 27.903
1102 | 41.119 | 27.907
1103 | 41.104 | 27.911
1104 | 41.117 | 27.911
1105 | 41.124 | 27.912
1106 | 41.127 | 27.914
1107 | 41.132 | 27.912
1108 | 41.132 | 27.917
1109 | 41.138 | 27.918
1110 | 41.145 | 27.921
1111 | 41.144 | 27.923
1112 | 41.14 | 27.923
1113 | 41.141 | 27.921
1114 | 41.141 | 27.925
1115 | 41.15 | 27.925
1116 | 41.14 | 27.924
1117 | 41.141 | 27.922
1118 | 41.14 | 27.923
1119 | 41.139 | 27.924
1120 | 41.141 | 27.925
1121 | 41.134 | 27.922
1122 | 41.134 | 27.925
1123 | 41.138 | 27.923
1124 | 41.14 | 27.925
1125 | 41.138 | 27.929
1126 | 41.144 | 27.934
1127 | 41.151 | 27.933
1128 | 41.151 | 27.934
1129 | 41.153 | 27.938
1130 | 41.162 | 27.94
1131 | 41.165 | 27.939
1132 | 41.171 | 27.943
1133 | 41.178 | 27.945
1134 | 41.171 | 27.944
1135 | 41.171 | 27.945
1136 | 41.168 | 27.944
1137 | 41.171 | 27.946
1138 | 41.166 | 27.95
1139 | 41.384 | 27.954
1140 | 41.473 | 27.958
1141 | 41.477 | 27.959
1142 | 41.47 | 27.96
1143 | 41.477 | 27.955
1144 | 41.484 | 27.957
1145 | 41.483 | 27.957
1146 | 41.485 | 27.958
1147 | 41.486 | 27.959
1148 | 41.495 | 27.956
1149 | 41.484 | 27.953
1150 | 41.47 | 27.948
1151 | 41.444 | 27.943
1152 | 41.432 | 27.942
1153 | 41.426 | 27.942
1154 | 41.429 | 27.94
1155 | 41.429 | 27.938
1156 | 41.43 | 27.94
1157 | 41.435 | 27.94
1158 | 41.432 | 27.941
1159 | 41.431 | 27.946
1160 | 41.429 | 27.946
1161 | 41.435 | 27.949
1162 | 41.442 | 27.953
1163 | 41.445 | 27.959
1164 | 41.449 | 27.958
1165 | 41.444 | 27.961
1166 | 41.454 | 27.962
1167 | 41.452 | 27.962
1168 | 41.46 | 27.964
1169 | 41.463 | 27.966
1170 | 41.463 | 27.968
1171 | 41.547 | 27.97
1172 | 41.722 | 27.966
1173 | 41.49 | 27.963
1174 | 41.469 | 27.962
1175 | 41.469 | 27.962
1176 | 41.454 | 27.96
1177 | 41.453 | 27.961
1178 | 41.451 | 27.962
1179 | 41.455 | 27.96
1180 | 41.451 | 27.961
1181 | 41.442 | 27.961
1182 | 41.446 | 27.966
1183 | 41.455 | 27.969
1184 | 41.46 | 27.971
1185 | 41.471 | 27.977
1186 | 41.466 | 27.976
1187 | 41.468 | 27.98
1188 | 41.484 | 27.982
1189 | 41.486 | 27.986
1190 | 41.485 | 27.99
1191 | 41.495 | 27.994
1192 | 41.495 | 27.996
1193 | 41.498 | 27.992
1194 | 41.481 | 27.983
1195 | 41.481 | 27.982
1196 | 41.473 | 27.982
1197 | 41.482 | 27.987
1198 | 41.491 | 27.987
1199 | 41.484 | 27.987
1200 | 41.485 | 27.984
1201 | 41.49 | 27.991
1202 | 41.496 | 27.994
1203 | 41.504 | 27.998
1204 | 41.509 | 27.999
1205 | 41.506 | 27.997
1206 | 41.514 | 28.002
1207 | 41.515 | 28.002
1208 | 41.517 | 28.001
1209 | 41.517 | 28.001
1210 | 41.521 | 28.002
1211 | 41.52 | 28.003
1212 | 41.524 | 28.006
1213 | 41.531 | 28.008
1214 | 41.535 | 28.007
1215 | 41.536 | 28.005
1216 | 41.535 | 28.008
1217 | 41.544 | 28.01
1218 | 41.545 | 28.012
1219 | 41.55 | 28.014
1220 | 41.559 | 28.017
1221 | 41.559 | 28.016
1222 | 41.56 | 28.019
1223 | 41.56 | 28.017
1224 | 41.57 | 28.017
1225 | 41.557 | 28.015
1226 | 41.551 | 28.013
1227 | 41.558 | 28.01
1228 | 41.563 | 28.008
1229 | 41.563 | 28.01
1230 | 41.556 | 28.01
1231 | 41.549 | 28.01
1232 | 41.549 | 28.006
1233 | 41.549 | 28.006
1234 | 41.545 | 28.006
1235 | 41.545 | 28.005
1236 | 41.563 | 28.012
1237 | 41.565 | 28.016
1238 | 41.57 | 28.021
1239 | 41.594 | 28.021
1240 | 41.581 | 28.018
1241 | 41.589 | 28.017
1242 | 41.585 | 28.021
1243 | 41.579 | 28.021
1244 | 41.598 | 28.021
1245 | 41.596 | 28.021
1246 | 41.596 | 28.02
1247 | 41.605 | 28.018
1248 | 41.611 | 28.019
1249 | 41.616 | 28.025
1250 | 41.626 | 28.022
1251 | 41.628 | 28.024
1252 | 41.623 | 28.021
1253 | 41.617 | 28.02
1254 | 41.601 | 28.02
1255 | 41.607 | 28.021
1256 | 41.604 | 28.022
1257 | 41.614 | 28.02
1258 | 41.611 | 28.023
1259 | 41.613 | 28.02
1260 | 41.604 | 28.02
1261 | 41.611 | 28.024
1262 | 41.607 | 28.026
1263 | 41.61 | 28.025
1264 | 41.607 | 28.026
1265 | 41.616 | 28.027
1266 | 41.62 | 28.026
1267 | 41.616 | 28.029
1268 | 41.614 | 28.03
1269 | 41.624 | 28.03
1270 | 41.626 | 28.033
1271 | 41.619 | 28.034
1272 | 41.632 | 28.034
1273 | 41.63 | 28.03
1274 | 41.621 | 28.031
1275 | 41.625 | 28.028
1276 | 41.624 | 28.034
1277 | 41.632 | 28.036
1278 | 41.638 | 28.038
1279 | 41.638 | 28.039
1280 | 41.645 | 28.037
1281 | 41.643 | 28.039
1282 | 41.633 | 28.039
1283 | 41.636 | 28.038
1284 | 41.632 | 28.042
1285 | 41.634 | 28.039
1286 | 41.627 | 28.038
1287 | 41.635 | 28.036
1288 | 41.639 | 28.036
1289 | 41.625 | 28.035
1290 | 41.633 | 28.039
1291 | 41.638 | 28.04
1292 | 41.634 | 28.042
1293 | 41.643 | 28.042
1294 | 41.635 | 28.038
1295 | 41.632 | 28.041
1296 | 41.645 | 28.041
1297 | 41.655 | 28.042
1298 | 41.645 | 28.043
1299 | 41.642 | 28.043
1300 | 41.646 | 28.045
1301 | 41.654 | 28.047
1302 | 41.644 | 28.042
1303 | 41.64 | 28.045
1304 | 41.648 | 28.048
1305 | 41.654 | 28.048
1306 | 41.651 | 28.05
1307 | 41.663 | 28.049
1308 | 41.662 | 28.048
1309 | 41.653 | 28.05
1310 | 41.614 | 28.042
1311 | 41.604 | 28.037
1312 | 41.619 | 28.037
1313 | 41.603 | 28.039
1314 | 41.605 | 28.038
1315 | 41.609 | 28.037
1316 | 41.6 | 28.034
1317 | 41.624 | 28.036
1318 | 41.629 | 28.039
1319 | 41.656 | 28.041
1320 | 41.644 | 28.041
1321 | 41.642 | 28.041
1322 | 41.635 | 28.043
1323 | 41.641 | 28.046
1324 | 41.634 | 28.045
1325 | 41.619 | 28.041
1326 | 41.61 | 28.039
1327 | 41.61 | 28.04
1328 | 41.609 | 28.04
1329 | 41.609 | 28.041
1330 | 41.617 | 28.039
1331 | 41.6 | 28.038
1332 | 41.6 | 28.035
1333 | 41.577 | 28.032
1334 | 41.572 | 28.03
1335 | 41.59 | 28.033
1336 | 41.588 | 28.035
1337 | 41.615 | 28.034
1338 | 41.626 | 28.034
1339 | 41.654 | 28.037
1340 | 41.65 | 28.042
1341 | 41.669 | 28.047
1342 | 41.667 | 28.045
1343 | 41.683 | 28.046
1344 | 41.662 | 28.04
1345 | 41.678 | 28.044
1346 | 41.67 | 28.041
1347 | 41.642 | 28.038
1348 | 41.651 | 28.035
1349 | 41.626 | 28.032
1350 | 41.63 | 28.029
1351 | 41.64 | 28.031
1352 | 41.626 | 28.027
1353 | 41.645 | 28.026
1354 | 41.66 | 28.03
1355 | 41.654 | 28.031
1356 | 41.642 | 28.032
1357 | 41.623 | 28.028
1358 | 41.631 | 28.027
1359 | 41.642 | 28.03
1360 | 41.643 | 28.029
1361 | 41.642 | 28.03
1362 | 41.645 | 28.028
1363 | 41.659 | 28.032
1364 | 41.657 | 28.033
1365 | 41.667 | 28.035
1366 | 41.657 | 28.037
1367 | 41.648 | 28.032
1368 | 41.637 | 28.029
1369 | 41.636 | 28.027
1370 | 41.652 | 28.03
1371 | 41.651 | 28.031
1372 | 41.651 | 28.029
1373 | 41.643 | 28.033
1374 | 41.642 | 28.032
1375 | 41.648 | 28.033
1376 | 41.647 | 28.029
1377 | 41.642 | 28.031
1378 | 41.654 | 28.033
1379 | 41.652 | 28.035
1380 | 41.663 | 28.036
1381 | 41.676 | 28.042
1382 | 41.665 | 28.044
1383 | 41.678 | 28.042
1384 | 41.687 | 28.045
1385 | 41.663 | 28.041
1386 | 41.689 | 28.043
1387 | 41.684 | 28.044
1388 | 41.672 | 28.044
1389 | 41.674 | 28.043
1390 | 41.681 | 28.041
1391 | 41.666 | 28.039
1392 | 41.681 | 28.041
1393 | 41.682 | 28.044
1394 | 41.66 | 28.039
1395 | 41.669 | 28.037
1396 | 41.676 | 28.039
1397 | 41.681 | 28.038
1398 | 41.685 | 28.04
1399 | 41.695 | 28.044
1400 | 41.699 | 28.046
1401 | 41.698 | 28.045
1402 | 41.673 | 28.042
1403 | 41.686 | 28.043
1404 | 41.694 | 28.046
1405 | 41.707 | 28.049
1406 | 41.701 | 28.049
1407 | 41.699 | 28.043
1408 | 41.694 | 28.043
1409 | 41.682 | 28.043
1410 | 41.691 | 28.045
1411 | 41.705 | 28.046
1412 | 41.706 | 28.049
1413 | 41.711 | 28.048
1414 | 41.702 | 28.047
1415 | 41.704 | 28.044
1416 | 41.702 | 28.047
1417 | 41.718 | 28.048
1418 | 41.719 | 28.048
1419 | 41.71 | 28.047
1420 | 41.723 | 28.048
1421 | 41.733 | 28.052
1422 | 41.715 | 28.05
1423 | 41.687 | 28.046
1424 | 41.684 | 28.039
1425 | 41.691 | 28.04
1426 | 41.702 | 28.043
1427 | 41.721 | 28.043
1428 | 41.699 | 28.045
1429 | 41.719 | 28.044
1430 | 41.707 | 28.048
1431 | 41.714 | 28.046
1432 | 41.702 | 28.046
1433 | 41.699 | 28.045
1434 | 41.716 | 28.046
1435 | 41.715 | 28.046
1436 | 41.72 | 28.046
1437 | 41.743 | 28.047
1438 | 41.746 | 28.052
1439 | 41.737 | 28.051
1440 | 41.711 | 28.046
1441 | 41.735 | 28.046
1442 | 41.732 | 28.049
1443 | 41.745 | 28.05
1444 | 41.741 | 28.05
1445 | 41.746 | 28.048
1446 | 41.755 | 28.052
1447 | 41.764 | 28.054
1448 | 41.754 | 28.054
1449 | 41.755 | 28.052
1450 | 41.723 | 28.05
1451 | 41.73 | 28.048
1452 | 41.765 | 28.05
1453 | 41.748 | 28.051
1454 | 41.748 | 28.052
1455 | 41.738 | 28.053
1456 | 41.752 | 28.051
1457 | 41.756 | 28.052
1458 | 41.768 | 28.054
1459 | 41.766 | 28.053
1460 | 41.745 | 28.053
1461 | 41.748 | 28.052
1462 | 41.747 | 28.051
1463 | 41.726 | 28.047
1464 | 41.747 | 28.047
1465 | 41.755 | 28.051
1466 | 41.74 | 28.051
1467 | 41.767 | 28.053
1468 | 41.765 | 28.055
1469 | 41.75 | 28.052
1470 | 41.752 | 28.052
1471 | 41.763 | 28.05
1472 | 41.775 | 28.056
1473 | 41.76 | 28.053
1474 | 41.773 | 28.055
1475 | 41.783 | 28.058
1476 | 41.778 | 28.057
1477 | 41.779 | 28.057
1478 | 41.77 | 28.058
1479 | 41.77 | 28.057
1480 | 41.801 | 28.061
1481 | 41.768 | 28.059
1482 | 41.773 | 28.058
1483 | 41.791 | 28.061
1484 | 41.789 | 28.063
1485 | 41.791 | 28.062
1486 | 41.779 | 28.061
1487 | 41.778 | 28.062
1488 | 41.788 | 28.062
1489 | 41.789 | 28.062
1490 | 41.784 | 28.062
1491 | 41.786 | 28.063
1492 | 41.763 | 28.06
1493 | 41.781 | 28.059
1494 | 41.782 | 28.063
1495 | 41.806 | 28.063
1496 | 41.789 | 28.067
1497 | 41.797 | 28.067
1498 | 41.796 | 28.068
1499 | 41.803 | 28.068
1500 | 41.805 | 28.071
1501 | 41.819 | 28.073
1502 | 41.811 | 28.072
1503 | 41.822 | 28.076
1504 | 41.813 | 28.074
1505 | 41.813 | 28.073
1506 | 41.808 | 28.074
1507 | 41.852 | 28.073
1508 | 41.861 | 28.073
1509 | 41.863 | 28.079
1510 | 41.862 | 28.083
1511 | 41.885 | 28.085
1512 | 41.879 | 28.089
1513 | 41.876 | 28.088
1514 | 41.884 | 28.09
1515 | 41.883 | 28.09
1516 | 41.885 | 28.091
1517 | 41.896 | 28.088
1518 | 41.882 | 28.09
1519 | 41.908 | 28.091
1520 | 41.9 | 28.093
1521 | 41.882 | 28.094
1522 | 41.881 | 28.094
1523 | 41.882 | 28.094
1524 | 41.886 | 28.095
1525 | 41.892 | 28.094
1526 | 41.902 | 28.097
1527 | 41.896 | 28.098
1528 | 41.879 | 28.1
1529 | 41.882 | 28.101
1530 | 41.878 | 28.102
1531 | 41.889 | 28.105
1532 | 41.893 | 28.107
1533 | 41.898 | 28.107
1534 | 41.886 | 28.109
1535 | 41.913 | 28.112
1536 | 41.91 | 28.11
1537 | 41.91 | 28.113
1538 | 41.931 | 28.113
1539 | 41.947 | 28.114
1540 | 41.937 | 28.114
1541 | 41.937 | 28.115
1542 | 41.938 | 28.117
1543 | 41.943 | 28.117
1544 | 41.936 | 28.117
1545 | 41.94 | 28.116
1546 | 41.955 | 28.118
1547 | 41.989 | 28.118
1548 | 41.944 | 28.117
1549 | 41.946 | 28.117
1550 | 41.952 | 28.119
1551 | 41.951 | 28.119
1552 | 41.951 | 28.117
1553 | 41.961 | 28.119
1554 | 41.986 | 28.12
1555 | 41.951 | 28.121
1556 | 41.957 | 28.124
1557 | 41.96 | 28.124
1558 | 41.973 | 28.124
1559 | 41.967 | 28.125
1560 | 41.964 | 28.128
1561 | 41.973 | 28.126
1562 | 41.983 | 28.129
1563 | 41.985 | 28.13
1564 | 41.959 | 28.131
1565 | 41.955 | 28.132
1566 | 41.96 | 28.132
1567 | 41.972 | 28.133
1568 | 41.971 | 28.13
1569 | 41.965 | 28.131
1570 | 41.975 | 28.134
1571 | 41.97 | 28.134
1572 | 41.978 | 28.134
1573 | 41.979 | 28.135
1574 | 41.979 | 28.137
1575 | 41.984 | 28.136
1576 | 41.983 | 28.134
1577 | 41.978 | 28.136
1578 | 41.993 | 28.135
1579 | 41.996 | 28.139
1580 | 42.011 | 28.139
1581 | 41.989 | 28.14
1582 | 41.992 | 28.138
1583 | 41.991 | 28.139
1584 | 41.983 | 28.138
1585 | 41.986 | 28.141
1586 | 41.992 | 28.144
1587 | 42 | 28.14
1588 | 41.998 | 28.14
1589 | 41.99 | 28.14
1590 | 41.992 | 28.142
1591 | 41.981 | 28.141
1592 | 41.986 | 28.14
1593 | 41.995 | 28.141
1594 | 41.982 | 28.143
1595 | 41.99 | 28.144
1596 | 41.995 | 28.144
1597 | 41.992 | 28.145
1598 | 41.99 | 28.147
1599 | 41.986 | 28.146
1600 | 42.012 | 28.147
1601 | 41.99 | 28.145
1602 | 41.976 | 28.146
1603 | 41.993 | 28.149
1604 | 41.99 | 28.15
1605 | 41.986 | 28.149
1606 | 41.999 | 28.148
1607 | 42 | 28.15
1608 | 41.985 | 28.152
1609 | 41.991 | 28.15
1610 | 41.988 | 28.151
1611 | 41.988 | 28.15
1612 | 41.994 | 28.154
1613 | 41.997 | 28.153
1614 | 42.002 | 28.153
1615 | 41.995 | 28.153
1616 | 41.995 | 28.153
1617 | 41.997 | 28.151
1618 | 41.988 | 28.153
1619 | 42.008 | 28.153
1620 | 42.006 | 28.158
1621 | 42.014 | 28.158
1622 | 42.022 | 28.157
1623 | 42.035 | 28.156
1624 | 42.027 | 28.158
1625 | 42.024 | 28.161
1626 | 42.032 | 28.162
1627 | 42.037 | 28.163
1628 | 42.04 | 28.16
1629 | 42.033 | 28.16
1630 | 42.036 | 28.157
1631 | 42.03 | 28.159
1632 | 42.02 | 28.159
1633 | 42.031 | 28.158
1634 | 42.016 | 28.16
1635 | 42.021 | 28.159
1636 | 42.023 | 28.161
1637 | 42.029 | 28.163
1638 | 42.046 | 28.166
1639 | 42.031 | 28.165
1640 | 42.038 | 28.165
1641 | 42.042 | 28.166
1642 | 42.033 | 28.165
1643 | 42.045 | 28.165
1644 | 42.043 | 28.166
1645 | 42.073 | 28.165
1646 | 42.041 | 28.164
1647 | 42.048 | 28.166
1648 | 42.051 | 28.168
1649 | 42.049 | 28.171
1650 | 42.059 | 28.171
1651 | 42.05 | 28.17
1652 | 42.04 | 28.168
1653 | 42.045 | 28.166
1654 | 42.036 | 28.165
1655 | 42.04 | 28.163
1656 | 42.059 | 28.161
1657 | 42.071 | 28.161
1658 | 42.067 | 28.16
1659 | 42.076 | 28.164
1660 | 42.07 | 28.162
1661 | 42.069 | 28.164
1662 | 42.078 | 28.165
1663 | 42.075 | 28.164
1664 | 42.087 | 28.166
1665 | 42.099 | 28.167
1666 | 42.09 | 28.167
1667 | 42.096 | 28.165
1668 | 42.088 | 28.162
1669 | 42.097 | 28.166
1670 | 42.094 | 28.168
1671 | 42.085 | 28.168
1672 | 42.085 | 28.17
1673 | 42.089 | 28.169
1674 | 42.084 | 28.164
1675 | 42.084 | 28.163
1676 | 42.11 | 28.165
1677 | 42.091 | 28.164
1678 | 42.091 | 28.166
1679 | 42.102 | 28.165
1680 | 42.102 | 28.169
1681 | 42.097 | 28.171
1682 | 42.106 | 28.174
1683 | 42.098 | 28.175
1684 | 42.114 | 28.179
1685 | 42.108 | 28.177
1686 | 42.104 | 28.174
1687 | 42.11 | 28.176
1688 | 42.129 | 28.177
1689 | 42.122 | 28.177
1690 | 42.127 | 28.179
1691 | 42.123 | 28.182
1692 | 42.129 | 28.186
1693 | 42.141 | 28.187
1694 | 42.135 | 28.184
1695 | 42.147 | 28.186
1696 | 42.151 | 28.187
1697 | 42.162 | 28.187
1698 | 42.166 | 28.19
1699 | 42.166 | 28.189
1700 | 42.161 | 28.187
1701 | 42.16 | 28.189
1702 | 42.163 | 28.191
1703 | 42.16 | 28.19
1704 | 42.17 | 28.188
1705 | 42.176 | 28.19
1706 | 42.19 | 28.189
1707 | 42.166 | 28.186
1708 | 42.159 | 28.184
1709 | 42.155 | 28.184
1710 | 42.155 | 28.185
1711 | 42.162 | 28.19
1712 | 42.168 | 28.194
1713 | 42.173 | 28.192
1714 | 42.225 | 28.194
1715 | 42.238 | 28.193
1716 | 42.237 | 28.191
1717 | 42.241 | 28.191
1718 | 42.237 | 28.194
1719 | 42.231 | 28.193
1720 | 42.225 | 28.189
1721 | 42.227 | 28.188
1722 | 42.221 | 28.189
1723 | 42.224 | 28.189
1724 | 42.217 | 28.19
1725 | 42.236 | 28.193
1726 | 42.234 | 28.19
1727 | 42.24 | 28.19
1728 | 42.236 | 28.193
1729 | 42.246 | 28.192
1730 | 42.249 | 28.193
1731 | 42.244 | 28.195
1732 | 42.262 | 28.196
1733 | 42.263 | 28.195
1734 | 42.259 | 28.198
1735 | 42.248 | 28.2
1736 | 42.244 | 28.2
1737 | 42.249 | 28.198
1738 | 42.241 | 28.203
1739 | 42.255 | 28.203
1740 | 42.246 | 28.203
1741 | 42.266 | 28.205
1742 | 42.263 | 28.207
1743 | 42.253 | 28.206
1744 | 42.257 | 28.209
1745 | 42.265 | 28.212
1746 | 42.267 | 28.215
1747 | 42.272 | 28.215
1748 | 42.269 | 28.216
1749 | 42.266 | 28.218
1750 | 42.281 | 28.221
1751 | 42.254 | 28.219
1752 | 42.257 | 28.219
1753 | 42.262 | 28.22
1754 | 42.249 | 28.217
1755 | 42.265 | 28.222
1756 | 42.279 | 28.223
1757 | 42.257 | 28.226
1758 | 42.259 | 28.226
1759 | 42.253 | 28.226
1760 | 42.248 | 28.224
1761 | 42.27 | 28.222
1762 | 42.258 | 28.219
1763 | 42.254 | 28.222
1764 | 42.234 | 28.224
1765 | 42.235 | 28.225
1766 | 42.238 | 28.228
1767 | 42.234 | 28.231
1768 | 42.237 | 28.229
1769 | 42.231 | 28.228
1770 | 42.236 | 28.231
1771 | 42.217 | 28.232
1772 | 42.255 | 28.234
1773 | 42.226 | 28.236
1774 | 42.231 | 28.237
1775 | 42.23 | 28.24
1776 | 42.238 | 28.24
1777 | 42.24 | 28.239
1778 | 42.24 | 28.242
1779 | 42.268 | 28.245
1780 | 42.303 | 28.241
1781 | 42.253 | 28.24
1782 | 42.256 | 28.24
1783 | 42.244 | 28.242
1784 | 42.26 | 28.242
1785 | 42.275 | 28.246
1786 | 42.277 | 28.246
1787 | 42.29 | 28.247
1788 | 42.289 | 28.246
1789 | 42.289 | 28.246
1790 | 42.275 | 28.242
1791 | 42.267 | 28.245
1792 | 42.285 | 28.248
1793 | 42.274 | 28.248
1794 | 42.278 | 28.25
1795 | 42.263 | 28.25
1796 | 42.254 | 28.253
1797 | 42.252 | 28.251
1798 | 42.245 | 28.251
1799 | 42.248 | 28.253
1800 | 42.254 | 28.255
1801 | 42.236 | 28.255
1802 | 42.237 | 28.253
1803 | 42.236 | 28.253
1804 | 42.255 | 28.254
1805 | 42.262 | 28.259
1806 | 42.26 | 28.259
1807 | 42.262 | 28.26
1808 | 42.265 | 28.264
1809 | 42.257 | 28.265
1810 | 42.297 | 28.265
1811 | 42.264 | 28.267
1812 | 42.3 | 28.268
1813 | 42.299 | 28.268
1814 | 42.3 | 28.271
1815 | 42.303 | 28.273
1816 | 42.303 | 28.269
1817 | 42.309 | 28.271
1818 | 42.335 | 28.272
1819 | 42.331 | 28.274
1820 | 42.331 | 28.274
1821 | 42.308 | 28.274
1822 | 42.303 | 28.274
1823 | 42.308 | 28.275
1824 | 42.326 | 28.276
1825 | 42.291 | 28.274
1826 | 42.308 | 28.277
1827 | 42.305 | 28.275
1828 | 42.325 | 28.278
1829 | 42.307 | 28.276
1830 | 42.287 | 28.278
1831 | 42.29 | 28.28
1832 | 42.301 | 28.28
1833 | 42.313 | 28.279
1834 | 42.296 | 28.283
1835 | 42.327 | 28.285
1836 | 42.314 | 28.288
1837 | 42.312 | 28.289
1838 | 42.341 | 28.29
1839 | 42.311 | 28.291
1840 | 42.314 | 28.293
1841 | 42.324 | 28.295
1842 | 42.304 | 28.294
1843 | 42.293 | 28.296
1844 | 42.297 | 28.298
1845 | 42.296 | 28.299
1846 | 42.299 | 28.302
1847 | 42.274 | 28.301
1848 | 42.274 | 28.303
1849 | 42.281 | 28.303
1850 | 42.268 | 28.306
1851 | 42.277 | 28.306
1852 | 42.303 | 28.307
1853 | 42.289 | 28.309
1854 | 42.28 | 28.31
1855 | 42.291 | 28.31
1856 | 42.276 | 28.311
1857 | 42.27 | 28.312
1858 | 42.256 | 28.314
1859 | 42.259 | 28.316
1860 | 42.267 | 28.316
1861 | 42.273 | 28.318
1862 | 42.29 | 28.318
1863 | 42.293 | 28.318
1864 | 42.333 | 28.314
1865 | 42.288 | 28.315
1866 | 42.291 | 28.318
1867 | 42.301 | 28.319
1868 | 42.283 | 28.317
1869 | 42.286 | 28.314
1870 | 42.29 | 28.318
1871 | 42.292 | 28.318
1872 | 42.307 | 28.317
1873 | 42.3 | 28.317
1874 | 42.3 | 28.319
1875 | 42.299 | 28.319
1876 | 42.306 | 28.321
1877 | 42.311 | 28.323
1878 | 42.314 | 28.325
1879 | 42.317 | 28.325
1880 | 42.318 | 28.324
1881 | 42.305 | 28.325
1882 | 42.322 | 28.325
1883 | 42.313 | 28.326
1884 | 42.31 | 28.325
1885 | 42.308 | 28.324
1886 | 42.294 | 28.322
1887 | 42.27 | 28.324
1888 | 42.259 | 28.322
1889 | 42.252 | 28.322
1890 | 42.237 | 28.322
1891 | 42.239 | 28.325
1892 | 42.237 | 28.327
1893 | 42.236 | 28.328
1894 | 42.255 | 28.325
1895 | 42.259 | 28.326
1896 | 42.337 | 28.322
1897 | 42.254 | 28.327
1898 | 42.247 | 28.325
1899 | 42.24 | 28.329
1900 | 42.258 | 28.334
1901 | 42.254 | 28.337
1902 | 42.258 | 28.337
1903 | 42.255 | 28.337
1904 | 42.261 | 28.337
1905 | 42.264 | 28.341
1906 | 42.281 | 28.343
1907 | 42.28 | 28.342
1908 | 42.274 | 28.344
1909 | 42.27 | 28.342
1910 | 42.28 | 28.344
1911 | 42.292 | 28.345
1912 | 42.301 | 28.346
1913 | 42.302 | 28.345
1914 | 42.315 | 28.343
1915 | 42.329 | 28.345
1916 | 42.334 | 28.348
1917 | 42.327 | 28.346
1918 | 42.331 | 28.345
1919 | 42.318 | 28.348
1920 | 42.3 | 28.344
1921 | 42.313 | 28.344
1922 | 42.326 | 28.342
1923 | 42.319 | 28.343
1924 | 42.308 | 28.344
1925 | 42.313 | 28.341
1926 | 42.31 | 28.339
1927 | 42.295 | 28.338
1928 | 42.289 | 28.336
1929 | 42.299 | 28.339
1930 | 42.293 | 28.339
1931 | 42.311 | 28.339
1932 | 42.309 | 28.338
1933 | 42.298 | 28.341
1934 | 42.319 | 28.341
1935 | 42.291 | 28.342
1936 | 42.294 | 28.344
1937 | 42.3 | 28.342
1938 | 42.314 | 28.346
1939 | 42.327 | 28.345
1940 | 42.307 | 28.345
1941 | 42.322 | 28.341
1942 | 42.321 | 28.342
1943 | 42.319 | 28.345
1944 | 42.328 | 28.345
1945 | 42.328 | 28.347
1946 | 42.318 | 28.35
1947 | 42.328 | 28.349
1948 | 42.372 | 28.35
1949 | 42.389 | 28.35
1950 | 42.42 | 28.349
1951 | 42.394 | 28.349
1952 | 42.406 | 28.346
1953 | 42.405 | 28.349
1954 | 42.411 | 28.352
1955 | 42.41 | 28.354
1956 | 42.415 | 28.354
1957 | 42.404 | 28.351
1958 | 42.434 | 28.353
1959 | 42.429 | 28.356
1960 | 42.448 | 28.357
1961 | 42.42 | 28.356
1962 | 42.403 | 28.353
1963 | 42.396 | 28.35
1964 | 42.386 | 28.347
1965 | 42.384 | 28.346
1966 | 42.386 | 28.344
1967 | 42.392 | 28.344
1968 | 42.389 | 28.348
1969 | 42.403 | 28.351
1970 | 42.394 | 28.354
1971 | 42.4 | 28.352
1972 | 42.41 | 28.354
1973 | 42.405 | 28.354
1974 | 42.443 | 28.359
1975 | 42.426 | 28.359
1976 | 42.412 | 28.357
1977 | 42.407 | 28.355
1978 | 42.392 | 28.359
1979 | 42.418 | 28.356
1980 | 42.423 | 28.352
1981 | 42.441 | 28.355
1982 | 42.461 | 28.358
1983 | 42.463 | 28.357
1984 | 42.437 | 28.358
1985 | 42.403 | 28.357
1986 | 42.42 | 28.357
1987 | 42.399 | 28.353
1988 | 42.418 | 28.357
1989 | 42.411 | 28.36
1990 | 42.438 | 28.361
1991 | 42.442 | 28.366
1992 | 42.445 | 28.369
1993 | 42.453 | 28.372
1994 | 42.439 | 28.372
1995 | 42.472 | 28.374
1996 | 42.495 | 28.375
1997 | 42.501 | 28.372
1998 | 42.476 | 28.366
1999 | 42.457 | 28.361
2000 | 42.468 | 28.363
2001 | 42.453 | 28.36
2002 | 42.479 | 28.363
2003 | 42.489 | 28.36
2004 | 42.493 | 28.361
2005 | 42.482 | 28.356
2006 | 42.478 | 28.356
2007 | 42.481 | 28.358
2008 | 42.467 | 28.359
2009 | 42.459 | 28.358
2010 | 42.469 | 28.362
2011 | 42.442 | 28.366
2012 | 42.453 | 28.366
2013 | 42.455 | 28.365
2014 | 42.466 | 28.367
2015 | 42.474 | 28.364
2016 | 42.465 | 28.364
2017 | 42.468 | 28.366
2018 | 42.472 | 28.369
2019 | 42.483 | 28.373
2020 | 42.458 | 28.376
2021 | 42.485 | 28.374
2022 | 42.481 | 28.37
2023 | 42.472 | 28.369
2024 | 42.471 | 28.372
2025 | 42.469 | 28.375
2026 | 42.502 | 28.376
2027 | 42.468 | 28.379
2028 | 42.473 | 28.383
2029 | 42.508 | 28.381
2030 | 42.507 | 28.384
2031 | 42.521 | 28.385
2032 | 42.511 | 28.386
2033 | 42.524 | 28.386
2034 | 42.519 | 28.383
2035 | 42.515 | 28.381
2036 | 42.505 | 28.376
2037 | 42.517 | 28.377
2038 | 42.489 | 28.375
2039 | 42.502 | 28.372
2040 | 42.483 | 28.37
2041 | 42.491 | 28.369
2042 | 42.487 | 28.367
2043 | 42.471 | 28.372
2044 | 42.474 | 28.374
2045 | 42.486 | 28.377
2046 | 42.486 | 28.374
2047 | 42.497 | 28.372
2048 | 42.511 | 28.374
2049 | 42.465 | 28.37
2050 | 42.457 | 28.372
2051 | 42.462 | 28.372
2052 | 42.471 | 28.375
2053 | 42.45 | 28.371
2054 | 42.457 | 28.373
2055 | 42.458 | 28.377
2056 | 42.471 | 28.375
2057 | 42.451 | 28.376
2058 | 42.467 | 28.376
2059 | 42.455 | 28.378
2060 | 42.458 | 28.38
2061 | 42.464 | 28.381
2062 | 42.486 | 28.384
2063 | 42.481 | 28.385
2064 | 42.468 | 28.383
2065 | 42.469 | 28.383
2066 | 42.475 | 28.382
2067 | 42.497 | 28.382
2068 | 42.473 | 28.386
2069 | 42.493 | 28.39
2070 | 42.488 | 28.39
2071 | 42.496 | 28.393
2072 | 42.5 | 28.393
2073 | 42.469 | 28.394
2074 | 42.467 | 28.394
2075 | 42.476 | 28.395
2076 | 42.49 | 28.394
2077 | 42.486 | 28.393
2078 | 42.491 | 28.39
2079 | 42.485 | 28.392
2080 | 42.494 | 28.397
2081 | 42.52 | 28.399
2082 | 42.514 | 28.399
2083 | 42.504 | 28.4
2084 | 42.502 | 28.405
2085 | 42.507 | 28.408
2086 | 42.518 | 28.41
2087 | 42.513 | 28.414
2088 | 42.515 | 28.413
2089 | 42.501 | 28.411
2090 | 42.485 | 28.411
2091 | 42.446 | 28.411
2092 | 42.429 | 28.413
2093 | 42.437 | 28.415
2094 | 42.442 | 28.414
2095 | 42.441 | 28.414
2096 | 42.45 | 28.415
2097 | 42.476 | 28.415
2098 | 42.456 | 28.414
2099 | 42.442 | 28.412
2100 | 42.442 | 28.417
2101 | 42.442 | 28.42
2102 | 42.447 | 28.42
2103 | 42.45 | 28.422
2104 | 42.452 | 28.424
2105 | 42.448 | 28.429
2106 | 42.461 | 28.427
2107 | 42.456 | 28.429
2108 | 42.464 | 28.428
2109 | 42.458 | 28.427
2110 | 42.468 | 28.425
2111 | 42.468 | 28.429
2112 | 42.494 | 28.434
2113 | 42.461 | 28.434
2114 | 42.467 | 28.434
2115 | 42.469 | 28.437
2116 | 42.469 | 28.437
2117 | 42.467 | 28.436
2118 | 42.461 | 28.437
2119 | 42.48 | 28.439
2120 | 42.476 | 28.44
2121 | 42.482 | 28.44
2122 | 42.47 | 28.442
2123 | 42.501 | 28.444
2124 | 42.479 | 28.446
2125 | 42.482 | 28.449
2126 | 42.474 | 28.443
2127 | 42.47 | 28.441
2128 | 42.481 | 28.444
2129 | 42.471 | 28.444
2130 | 42.474 | 28.443
2131 | 42.469 | 28.445
2132 | 42.468 | 28.443
2133 | 42.476 | 28.446
2134 | 42.46 | 28.447
2135 | 42.467 | 28.448
2136 | 42.467 | 28.445
2137 | 42.468 | 28.447
2138 | 42.47 | 28.449
2139 | 42.473 | 28.448
2140 | 42.493 | 28.447
2141 | 42.46 | 28.445
2142 | 42.47 | 28.443
2143 | 42.468 | 28.44
2144 | 42.464 | 28.439
2145 | 42.463 | 28.438
2146 | 42.479 | 28.437
2147 | 42.475 | 28.438
2148 | 42.484 | 28.439
2149 | 42.466 | 28.434
2150 | 42.471 | 28.433
2151 | 42.47 | 28.431
2152 | 42.484 | 28.439
2153 | 42.493 | 28.438
2154 | 42.485 | 28.442
2155 | 42.486 | 28.438
2156 | 42.485 | 28.44
2157 | 42.486 | 28.443
2158 | 42.477 | 28.449
2159 | 42.493 | 28.455
2160 | 42.492 | 28.457
2161 | 42.495 | 28.457
2162 | 42.484 | 28.457
2163 | 42.487 | 28.456
2164 | 42.491 | 28.452
2165 | 42.496 | 28.45
2166 | 42.499 | 28.449
2167 | 42.491 | 28.452
2168 | 42.52 | 28.453
2169 | 42.526 | 28.454
2170 | 42.522 | 28.454
2171 | 42.526 | 28.453
2172 | 42.519 | 28.444
2173 | 42.52 | 28.444
2174 | 42.552 | 28.451
2175 | 42.527 | 28.455
2176 | 42.515 | 28.458
2177 | 42.536 | 28.462
2178 | 42.533 | 28.462
2179 | 42.563 | 28.464
2180 | 42.551 | 28.464
2181 | 42.564 | 28.464
2182 | 42.568 | 28.463
2183 | 42.513 | 28.461
2184 | 42.501 | 28.457
2185 | 42.512 | 28.458
2186 | 42.544 | 28.458
2187 | 42.537 | 28.457
2188 | 42.531 | 28.46
2189 | 42.553 | 28.461
2190 | 42.502 | 28.464
2191 | 42.482 | 28.464
2192 | 42.472 | 28.464
2193 | 42.475 | 28.468
2194 | 42.48 | 28.467
2195 | 42.481 | 28.467
2196 | 42.474 | 28.468
2197 | 42.48 | 28.47
2198 | 42.486 | 28.473
2199 | 42.485 | 28.475
2200 | 42.517 | 28.478
2201 | 42.495 | 28.478
2202 | 42.491 | 28.479
2203 | 42.5 | 28.482
2204 | 42.506 | 28.478
2205 | 42.496 | 28.48
2206 | 42.506 | 28.481
2207 | 42.501 | 28.482
2208 | 42.523 | 28.48
2209 | 42.532 | 28.481
2210 | 42.515 | 28.48
2211 | 42.512 | 28.477
2212 | 42.499 | 28.471
2213 | 42.49 | 28.47
2214 | 42.501 | 28.467
2215 | 42.499 | 28.466
2216 | 42.496 | 28.469
2217 | 42.494 | 28.466
2218 | 42.497 | 28.465
2219 | 42.508 | 28.469
2220 | 42.52 | 28.464
2221 | 42.535 | 28.468
2222 | 42.515 | 28.467
2223 | 42.506 | 28.466
2224 | 42.501 | 28.462
2225 | 42.513 | 28.469
2226 | 42.514 | 28.474
2227 | 42.524 | 28.475
2228 | 42.512 | 28.474
2229 | 42.502 | 28.469
2230 | 42.495 | 28.469
2231 | 42.507 | 28.468
2232 | 42.502 | 28.471
2233 | 42.534 | 28.47
2234 | 42.501 | 28.47
2235 | 42.5 | 28.468
2236 | 42.514 | 28.472
2237 | 42.515 | 28.473
2238 | 42.493 | 28.464
2239 | 42.49 | 28.463
2240 | 42.525 | 28.46
2241 | 42.491 | 28.462
2242 | 42.484 | 28.459
2243 | 42.487 | 28.463
2244 | 42.485 | 28.467
2245 | 42.496 | 28.466
2246 | 42.492 | 28.46
2247 | 42.492 | 28.463
2248 | 42.483 | 28.463
2249 | 42.494 | 28.464
2250 | 42.494 | 28.467
2251 | 42.496 | 28.467
2252 | 42.521 | 28.467
2253 | 42.512 | 28.465
2254 | 42.509 | 28.467
2255 | 42.496 | 28.469
2256 | 42.494 | 28.471
2257 | 42.486 | 28.468
2258 | 42.495 | 28.471
2259 | 42.491 | 28.468
2260 | 42.485 | 28.473
2261 | 42.496 | 28.471
2262 | 42.482 | 28.469
2263 | 42.5 | 28.47
2264 | 42.487 | 28.469
2265 | 42.476 | 28.468
2266 | 42.492 | 28.471
2267 | 42.475 | 28.471
2268 | 42.477 | 28.472
2269 | 42.491 | 28.472
2270 | 42.483 | 28.472
2271 | 42.489 | 28.476
2272 | 42.498 | 28.483
2273 | 42.502 | 28.482
2274 | 42.523 | 28.483
2275 | 42.494 | 28.48
2276 | 42.509 | 28.48
2277 | 42.524 | 28.483
2278 | 42.5 | 28.48
2279 | 42.505 | 28.482
2280 | 42.512 | 28.488
2281 | 42.522 | 28.485
2282 | 42.521 | 28.487
2283 | 42.497 | 28.486
2284 | 42.487 | 28.485
2285 | 42.487 | 28.484
2286 | 42.512 | 28.487
2287 | 42.483 | 28.481
2288 | 42.474 | 28.478
2289 | 42.48 | 28.478
2290 | 42.482 | 28.48
2291 | 42.473 | 28.479
2292 | 42.488 | 28.483
2293 | 42.477 | 28.487
2294 | 42.494 | 28.492
2295 | 42.499 | 28.49
2296 | 42.491 | 28.489
2297 | 42.494 | 28.489
2298 | 42.513 | 28.491
2299 | 42.486 | 28.493
2300 | 42.498 | 28.496
2301 | 42.5 | 28.497
2302 | 42.496 | 28.494
2303 | 42.487 | 28.495
2304 | 42.496 | 28.495
2305 | 42.518 | 28.5
2306 | 42.491 | 28.501
2307 | 42.497 | 28.5
2308 | 42.492 | 28.498
2309 | 42.499 | 28.504
2310 | 42.51 | 28.507
2311 | 42.498 | 28.506
2312 | 42.512 | 28.504
2313 | 42.498 | 28.505
2314 | 42.525 | 28.503
2315 | 42.522 | 28.507
2316 | 42.505 | 28.508
2317 | 42.508 | 28.509
2318 | 42.51 | 28.509
2319 | 42.52 | 28.512
2320 | 42.508 | 28.512
2321 | 42.514 | 28.515
2322 | 42.514 | 28.51
2323 | 42.508 | 28.508
2324 | 42.512 | 28.503
2325 | 42.508 | 28.505
2326 | 42.512 | 28.507
2327 | 42.531 | 28.503
2328 | 42.504 | 28.507
2329 | 42.519 | 28.509
2330 | 42.515 | 28.508
2331 | 42.503 | 28.51
2332 | 42.515 | 28.515
2333 | 42.52 | 28.516
2334 | 42.512 | 28.518
2335 | 42.536 | 28.519
2336 | 42.495 | 28.517
2337 | 42.503 | 28.509
2338 | 42.493 | 28.508
2339 | 42.496 | 28.505
2340 | 42.494 | 28.506
2341 | 42.486 | 28.505
2342 | 42.512 | 28.505
2343 | 42.493 | 28.504
2344 | 42.495 | 28.503
2345 | 42.491 | 28.509
2346 | 42.498 | 28.51
2347 | 42.492 | 28.511
2348 | 42.503 | 28.515
2349 | 42.508 | 28.518
2350 | 42.521 | 28.524
2351 | 42.527 | 28.528
2352 | 42.535 | 28.528
2353 | 42.534 | 28.53
2354 | 42.548 | 28.532
2355 | 42.558 | 28.528
2356 | 42.553 | 28.526
2357 | 42.554 | 28.526
2358 | 42.556 | 28.53
2359 | 42.574 | 28.531
2360 | 42.567 | 28.534
2361 | 42.551 | 28.538
2362 | 42.559 | 28.534
2363 | 42.564 | 28.53
2364 | 42.552 | 28.524
2365 | 42.546 | 28.526
2366 | 42.546 | 28.528
2367 | 42.561 | 28.526
2368 | 42.565 | 28.525
2369 | 42.551 | 28.519
2370 | 42.545 | 28.512
2371 | 42.53 | 28.51
2372 | 42.554 | 28.514
2373 | 42.536 | 28.516
2374 | 42.551 | 28.515
2375 | 42.543 | 28.516
2376 | 42.555 | 28.518
2377 | 42.554 | 28.517
2378 | 42.534 | 28.515
2379 | 42.567 | 28.516
2380 | 42.555 | 28.518
2381 | 42.554 | 28.519
2382 | 42.556 | 28.517
2383 | 42.542 | 28.519
2384 | 42.534 | 28.519
2385 | 42.579 | 28.521
2386 | 42.555 | 28.521
2387 | 42.563 | 28.525
2388 | 42.567 | 28.525
2389 | 42.564 | 28.524
2390 | 42.603 | 28.525
2391 | 42.57 | 28.53
2392 | 42.563 | 28.53
2393 | 42.566 | 28.528
2394 | 42.556 | 28.528
2395 | 42.555 | 28.526
2396 | 42.546 | 28.522
2397 | 42.556 | 28.524
2398 | 42.55 | 28.523
2399 | 42.554 | 28.525
2400 | 42.544 | 28.525
2401 | 42.552 | 28.522
2402 | 42.547 | 28.519
2403 | 42.533 | 28.519
2404 | 42.535 | 28.521
2405 | 42.549 | 28.524
2406 | 42.543 | 28.523
2407 | 42.544 | 28.526
2408 | 42.545 | 28.527
2409 | 42.538 | 28.527
2410 | 42.532 | 28.527
2411 | 42.536 | 28.528
2412 | 42.541 | 28.529
2413 | 42.532 | 28.528
2414 | 42.544 | 28.53
2415 | 42.537 | 28.536
2416 | 42.546 | 28.537
2417 | 42.538 | 28.536
2418 | 42.579 | 28.538
2419 | 42.545 | 28.54
2420 | 42.553 | 28.539
2421 | 42.554 | 28.537
2422 | 42.552 | 28.542
2423 | 42.554 | 28.544
2424 | 42.562 | 28.547
2425 | 42.558 | 28.548
2426 | 42.553 | 28.546
2427 | 42.561 | 28.541
2428 | 42.543 | 28.539
2429 | 42.582 | 28.537
2430 | 42.546 | 28.536
2431 | 42.552 | 28.541
2432 | 42.553 | 28.537
2433 | 42.54 | 28.533
2434 | 42.536 | 28.532
2435 | 42.555 | 28.537
2436 | 42.541 | 28.542
2437 | 42.562 | 28.54
2438 | 42.545 | 28.539
2439 | 42.539 | 28.539
2440 | 42.558 | 28.544
2441 | 42.544 | 28.541
2442 | 42.56 | 28.539
2443 | 42.548 | 28.539
2444 | 42.543 | 28.537
2445 | 42.539 | 28.533
2446 | 42.531 | 28.535
2447 | 42.551 | 28.531
2448 | 42.54 | 28.533
2449 | 42.581 | 28.539
2450 | 42.552 | 28.542
2451 | 42.556 | 28.54
2452 | 42.545 | 28.541
2453 | 42.546 | 28.539
2454 | 42.537 | 28.539
2455 | 42.571 | 28.543
2456 | 42.549 | 28.545
2457 | 42.562 | 28.548
2458 | 42.563 | 28.546
2459 | 42.561 | 28.549
2460 | 42.57 | 28.555
2461 | 42.573 | 28.555
2462 | 42.578 | 28.555
2463 | 42.602 | 28.56
2464 | 42.59 | 28.558
2465 | 42.597 | 28.563
2466 | 42.595 | 28.566
2467 | 42.587 | 28.562
2468 | 42.594 | 28.56
2469 | 42.585 | 28.558
2470 | 42.585 | 28.557
2471 | 42.578 | 28.554
2472 | 42.582 | 28.557
2473 | 42.601 | 28.563
2474 | 42.601 | 28.561
2475 | 42.597 | 28.562
2476 | 42.592 | 28.563
2477 | 42.628 | 28.568
2478 | 42.62 | 28.571
2479 | 42.63 | 28.572
2480 | 42.631 | 28.574
2481 | 42.644 | 28.574
2482 | 42.613 | 28.563
2483 | 42.609 | 28.56
2484 | 42.624 | 28.562
2485 | 42.624 | 28.561
2486 | 42.605 | 28.564
2487 | 42.615 | 28.568
2488 | 42.614 | 28.575
2489 | 42.627 | 28.58
2490 | 42.621 | 28.577
2491 | 42.62 | 28.573
2492 | 42.61 | 28.57
2493 | 42.606 | 28.569
2494 | 42.616 | 28.568
2495 | 42.661 | 28.568
2496 | 42.628 | 28.565
2497 | 42.625 | 28.563
2498 | 42.631 | 28.569
2499 | 42.637 | 28.572
2500 | 42.645 | 28.577
2501 | 42.643 | 28.579
2502 | 42.654 | 28.578
2503 | 42.653 | 28.577
2504 | 42.649 | 28.575
2505 | 42.627 | 28.578
2506 | 42.623 | 28.576
2507 | 42.616 | 28.571
2508 | 42.638 | 28.572
2509 | 42.603 | 28.572
2510 | 42.635 | 28.569
2511 | 42.616 | 28.577
2512 | 42.63 | 28.581
2513 | 42.629 | 28.585
2514 | 42.617 | 28.579
2515 | 42.642 | 28.575
2516 | 42.61 | 28.572
2517 | 42.613 | 28.573
2518 | 42.621 | 28.571
2519 | 42.666 | 28.58
2520 | 42.635 | 28.582
2521 | 42.634 | 28.587
2522 | 42.627 | 28.587
2523 | 42.629 | 28.587
2524 | 42.626 | 28.582
2525 | 42.621 | 28.577
2526 | 42.621 | 28.579
2527 | 42.617 | 28.58
2528 | 42.624 | 28.586
2529 | 42.614 | 28.586
2530 | 42.629 | 28.581
2531 | 42.626 | 28.576
2532 | 42.619 | 28.578
2533 | 42.629 | 28.583
2534 | 42.634 | 28.58
2535 | 42.637 | 28.585
2536 | 42.61 | 28.581
2537 | 42.605 | 28.581
2538 | 42.632 | 28.582
2539 | 42.665 | 28.579
2540 | 42.658 | 28.583
2541 | 42.653 | 28.585
2542 | 42.75 | 28.587
2543 | 42.717 | 28.584
2544 | 42.612 | 28.586
2545 | 42.654 | 28.585
2546 | 43.127 | 28.582
2547 | 42.84 | 28.585
2548 | 42.668 | 28.586
2549 | 42.647 | 28.587
2550 | 42.633 | 28.584
2551 | 42.635 | 28.581
2552 | 42.648 | 28.585
2553 | 42.665 | 28.589
2554 | 42.671 | 28.593
2555 | 42.681 | 28.588
2556 | 42.762 | 28.591
2557 | 42.805 | 28.592
2558 | 42.799 | 28.589
2559 | 42.783 | 28.584
2560 | 42.775 | 28.581
2561 | 42.769 | 28.582
2562 | 42.755 | 28.58
2563 | 42.759 | 28.581
2564 | 42.777 | 28.59
2565 | 42.781 | 28.591
2566 | 42.779 | 28.587
2567 | 42.78 | 28.589
2568 | 42.773 | 28.588
2569 | 42.798 | 28.592
2570 | 42.802 | 28.594
2571 | 42.794 | 28.597
2572 | 42.787 | 28.59
2573 | 42.783 | 28.585
2574 | 42.772 | 28.586
2575 | 42.776 | 28.586
2576 | 42.797 | 28.59
2577 | 42.779 | 28.587
2578 | 42.786 | 28.591
2579 | 42.796 | 28.597
2580 | 42.783 | 28.59
2581 | 42.778 | 28.59
2582 | 42.791 | 28.593
2583 | 42.803 | 28.596
2584 | 42.794 | 28.592
2585 | 42.8 | 28.594
2586 | 42.81 | 28.592
2587 | 42.792 | 28.593
2588 | 42.793 | 28.595
2589 | 42.788 | 28.597
2590 | 42.806 | 28.596
2591 | 42.787 | 28.598
2592 | 42.799 | 28.601
2593 | 42.838 | 28.603
2594 | 43.129 | 28.608
2595 | 42.882 | 28.612
2596 | 42.829 | 28.614
2597 | 42.828 | 28.611
2598 | 42.816 | 28.603
2599 | 42.808 | 28.597
2600 | 42.806 | 28.6
2601 | 42.802 | 28.6
2602 | 42.799 | 28.6
2603 | 42.796 | 28.604
2604 | 42.805 | 28.605
2605 | 42.797 | 28.609
2606 | 42.796 | 28.611
2607 | 42.76 | 28.608
2608 | 42.723 | 28.61
2609 | 42.689 | 28.616
2610 | 42.688 | 28.618
2611 | 42.681 | 28.619
2612 | 42.687 | 28.626
2613 | 42.682 | 28.628
2614 | 42.687 | 28.632
2615 | 42.679 | 28.625
2616 | 42.683 | 28.629
2617 | 42.689 | 28.633
2618 | 42.693 | 28.631
2619 | 42.68 | 28.631
2620 | 42.688 | 28.636
2621 | 42.663 | 28.639
2622 | 42.925 | 28.639
2623 | 42.769 | 28.639
2624 | 42.653 | 28.639
2625 | 42.606 | 28.64
2626 | 42.576 | 28.632
2627 | 42.553 | 28.626
2628 | 42.597 | 28.625
2629 | 42.559 | 28.622
2630 | 42.619 | 28.614
2631 | 42.694 | 28.615
2632 | 42.694 | 28.618
2633 | 42.697 | 28.617
2634 | 42.704 | 28.615
2635 | 42.718 | 28.619
2636 | 42.711 | 28.621
2637 | 42.735 | 28.627
2638 | 42.724 | 28.63
2639 | 42.696 | 28.628
2640 | 42.604 | 28.63
2641 | 42.537 | 28.627
2642 | 42.491 | 28.621
2643 | 42.487 | 28.619
2644 | 42.496 | 28.617
2645 | 42.492 | 28.614
2646 | 42.487 | 28.612
2647 | 42.512 | 28.614
2648 | 42.5 | 28.618
2649 | 42.452 | 28.609
2650 | 42.454 | 28.607
2651 | 42.493 | 28.615
2652 | 42.507 | 28.623
2653 | 42.494 | 28.626
2654 | 42.483 | 28.624
2655 | 42.498 | 28.624
2656 | 42.548 | 28.634
2657 | 42.565 | 28.645
2658 | 42.545 | 28.641
2659 | 42.501 | 28.638
2660 | 42.511 | 28.63
2661 | 42.557 | 28.631
2662 | 42.519 | 28.63
2663 | 42.512 | 28.625
2664 | 42.525 | 28.623
2665 | 42.592 | 28.63
2666 | 42.53 | 28.621
2667 | 42.457 | 28.611
2668 | 42.431 | 28.614
2669 | 42.413 | 28.614
2670 | 42.47 | 28.619
2671 | 42.443 | 28.617
2672 | 42.424 | 28.613
2673 | 42.475 | 28.619
2674 | 42.47 | 28.617
2675 | 42.479 | 28.62
2676 | 42.446 | 28.616
2677 | 42.48 | 28.618
2678 | 42.483 | 28.622
2679 | 42.405 | 28.61
2680 | 42.436 | 28.607
2681 | 42.421 | 28.608
2682 | 42.43 | 28.605
2683 | 42.422 | 28.61
2684 | 42.431 | 28.61
2685 | 42.458 | 28.619
2686 | 42.483 | 28.626
2687 | 42.484 | 28.626
2688 | 42.515 | 28.628
2689 | 42.521 | 28.631
2690 | 42.52 | 28.632
2691 | 42.485 | 28.63
2692 | 42.413 | 28.631
2693 | 42.392 | 28.63
2694 | 42.401 | 28.626
2695 | 42.376 | 28.625
2696 | 42.357 | 28.626
2697 | 42.356 | 28.623
2698 | 42.372 | 28.621
2699 | 42.336 | 28.622
2700 | 42.317 | 28.616
2701 | 42.34 | 28.621
2702 | 42.386 | 28.627
2703 | 42.353 | 28.627
2704 | 42.337 | 28.623
2705 | 42.366 | 28.629
2706 | 42.397 | 28.633
2707 | 42.299 | 28.629
2708 | 42.326 | 28.629
2709 | 42.323 | 28.633
2710 | 42.343 | 28.635
2711 | 42.328 | 28.637
2712 | 42.358 | 28.639
2713 | 42.426 | 28.64
2714 | 42.341 | 28.646
2715 | 42.349 | 28.639
2716 | 42.305 | 28.643
2717 | 42.328 | 28.648
2718 | 42.305 | 28.645
2719 | 42.347 | 28.644
2720 | 42.317 | 28.647
2721 | 42.295 | 28.647
2722 | 42.292 | 28.647
2723 | 42.311 | 28.646
2724 | 42.331 | 28.649
2725 | 42.321 | 28.648
2726 | 42.302 | 28.65
2727 | 42.272 | 28.641
2728 | 42.252 | 28.637
2729 | 42.304 | 28.643
2730 | 42.318 | 28.646
2731 | 42.29 | 28.646
2732 | 42.34 | 28.65
2733 | 42.293 | 28.649
2734 | 42.287 | 28.645
2735 | 42.299 | 28.647
2736 | 42.383 | 28.655
2737 | 42.503 | 28.653
2738 | 42.654 | 28.653
2739 | 42.714 | 28.656

## Borehole parameters
Thermal response test data supplied by the contractor
Parameters | Units | DMU -Test Borehole
Borehole depth | m | 100
Borehole diameter | m | 0.125
pipe material& specification | -- | PE SDR11
Spacing between pipe | -- | Average
Pipe inner diameter | m | 0.026
Data point time interval | minutes | 1
Constant power supply | W | 5734
The values used in the estimation of effective thermal properties
Parameters | Units | Value
Initial ground temperature | °C | 11.7
Volumetric heat capacity of pipe | MJ/(m3.K) | 1.805
Pipe thermal conductivity | W/(m.K) | 0.4
Liquid thermal conductivity | W/(m.K) | 0.61546
Liquid kinematic viscosity | m2/s | 0.0008009
Liquid flow rate | m3/s | 0.0001
Number of data points | counts | 2739
Grout:
The borehole is partly backfilled with drill cuttings and grouted over the top 25m. Grout thermal conductivity has been specified by the installation contractor to be 2.0 Wm-1K-1 .
Geology:
The rough geology of the DMU leicester site has been collected from BGS website, and it is observed that the site's common surface geology includes gravel and sandy clay, and bed rock includes red marl, sand stone and mud stone.

## Estimated thermal properties
Thermal Property | Estimated effective values
K soil (W/(m.K)) | 3.447
K grout (W/(m.K)) | 0.656
Volumetric specific heat capacity - Soil (J/(m3.K)) | 2576400
Volumetric specific heat capacity- Grout (J/(m3.K)) | 2700750