## Bypass data
Duct dimensions for single rack tests |  | Variables assumed for % bypass calculations
Width (mm) | Height (mm) | IT power consumption (kW) | ΔT (K) | cp (kJ.kg-1.K-1) | ρ (kg.m3) | Flow rate required through rack (m3/s) = IT power consumption/(ΔT x cp x ρ)
232 | 97 | 12 | 12.5 | 1.005 | 1.2 | 0.796
Single rack test 1
ΔpCH | Air Speed (m/s) | Bypass flow rate (m3/s) = Air Speed x Width x Height | Bypass %
10 | 5.9 | 0.13277 | 14.3
18 | 7.9 | 0.17778 | 18.3
23 | 9.3 | 0.20929 | 20.8
Single rack test 2
ΔpCH | Air Speed (m/s) | Bypass flow rate (m3/s) = Air Speed x Width x Height | Bypass %
2.6 | 1.1 | 0.024754 | 3.0161
4.7 | 1.5 | 0.033756 | 4.0682
6.8 | 1.7 | 0.038257 | 4.5857
9.9 | 2.2 | 0.049509 | 5.8555
14.9 | 3 | 0.067512 | 7.8183
20.6 | 4 | 0.090016 | 10.1596
Single rack test 3
ΔpCH | Air Speed (m/s) | Bypass flow rate (m3/s) = Air Speed x Width x Height | Bypass %
3 | 0.35 | 0.0078764 | 0.9798
6.5 | 0.55 | 0.012377 | 1.5311
11.5 | 0.7 | 0.015753 | 1.9406
19 | 0.9 | 0.020254 | 2.4813
Test data centre | See raw data (air speed measurements) and flow rate calculations in columns I-BD | [15 empty] | Upper sector | [5 empty] | Lower sector | [5 empty] | Left hand sector | [5 empty] | Right hand sector
ΔpCH | Estimated cube leakage (m3.s-1) | Supply air flow rate to test data centre (m3.s-1) | Calculated bypass flow rate (m3.s-1) | Bypass % | [12 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
1.1 | 0 | 0.013575 | 0.013575 | 0.42454 |  |  | Calculations to convert speed measurements to flow rates start in cell AB28
3.1 | 9.5882e-05 | 0.040396 | 0.0403 | 1.2499 |  |  | ΔpCH | Air speed measurements within supply air duct (m/s)
7.2 | 0.00088212 | 0.057634 | 0.056752 | 1.7512 |  |  | 30.5 |  |  |  |  | 3.8
13 | 0.004446 | 0.086935 | 0.082489 | 2.5253 | [7 empty] | 3.5 |  |  |  |  | 0.1435 | 0.1525 | 3.8 | 0 |  | 0.0039351 | 0.1435 | 0.1525 | 3 | 0 |  | 0.0031066 | 0.1435 | 0.1525 | 3.4 | 0 |  | 0.0035209 | 0.1435 | 0.1525 | 2.3 | 0 |  | 0.0023818
19.7 | 0.0074511 | 0.11376 | 0.10631 | 3.2309 | [7 empty] | 3.1 |  |  |  |  | 0.105 | 0.1435 | 3.5 | 3.8 |  | 0.027485 | 0.105 | 0.1435 | 2.3 | 3 |  | 0.020048 | 0.105 | 0.1435 | 2.6 | 3.4 |  | 0.022698 | 0.105 | 0.1435 | 1.3 | 2.3 |  | 0.013719
[12 empty] | 2.4 |  |  |  |  | 0.07 | 0.105 | 3.1 | 3.5 |  | 0.015939 | 0.07 | 0.105 | 2.1 | 2.3 |  | 0.010615 | 0.07 | 0.105 | 2.3 | 2.6 |  | 0.011834 | 0.07 | 0.105 | 2.1 | 1.3 |  | 0.0080497
[8 empty] | 3.4 | 2.6 | 2.3 | 2.3 | 2.6 | 2.6 | 2.1 | 1.3 | 2.3 | 0.035 | 0.07 | 2.4 | 3.1 |  | 0.0080497 | 0.035 | 0.07 | 1.5 | 2.1 |  | 0.0052916 | 0.035 | 0.07 | 2.3 | 2.3 |  | 0.0066386 | 0.035 | 0.07 | 2.6 | 2.1 |  | 0.0067027
[12 empty] | 1.5 |  |  |  |  | 0 | 0.035 | 2.6 | 2.4 |  | 0.0023732 | 0 | 0.035 | 2.6 | 1.5 |  | 0.0017959 | 0 | 0.035 | 2.6 | 2.3 |  | 0.0023091 | 0 | 0.035 | 2.6 | 2.6 |  | 0.0025015
2.1
[12 empty] | 2.3 | [8 empty] | Subtotal=> | 0.057782 |  |  |  |  | Subtotal=> | 0.040858 |  |  |  |  | Subtotal=> | 0.047 |  |  |  |  | Subtotal=> | 0.033355 | 0.17899
3
[17 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 1.1 |  |  |  |  | 0.1 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 0.2 |  |  |  |  | 0.1435 | 0.1525 | 0.1 | 0 |  | 0.00010355 | 0.1435 | 0.1525 | 0.3 | 0 |  | 0.00031066 | 0.1435 | 0.1525 | 0.1 | 0 |  | 0.00010355 | 0.1435 | 0.1525 | 0.1 | 0 |  | 0.00010355
[12 empty] | 0.1 |  |  |  |  | 0.105 | 0.1435 | 0.2 | 0.1 |  | 0.0011077 | 0.105 | 0.1435 | 0.3 | 0.3 |  | 0.0022542 | 0.105 | 0.1435 | 0.2 | 0.1 |  | 0.0011077 | 0.105 | 0.1435 | 0.2 | 0.1 |  | 0.0011077
[12 empty] | 0.2 |  |  |  |  | 0.07 | 0.105 | 0.1 | 0.2 |  | 0.00073762 | 0.07 | 0.105 | 0.3 | 0.3 |  | 0.0014432 | 0.07 | 0.105 | 0.2 | 0.2 |  | 0.00096211 | 0.07 | 0.105 | 0.2 | 0.2 |  | 0.00096211
[8 empty] | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.035 | 0.07 | 0.2 | 0.1 |  | 0.00041692 | 0.035 | 0.07 | 0.3 | 0.3 |  | 0.0008659 | 0.035 | 0.07 | 0.2 | 0.2 |  | 0.00057727 | 0.035 | 0.07 | 0.2 | 0.2 |  | 0.00057727
[12 empty] | 0.3 |  |  |  |  | 0 | 0.035 | 0.2 | 0.2 |  | 0.00019242 | 0 | 0.035 | 0.2 | 0.3 |  | 0.00025656 | 0 | 0.035 | 0.2 | 0.2 |  | 0.00019242 | 0 | 0.035 | 0.2 | 0.2 |  | 0.00019242
0.3
[12 empty] | 0.3 | [8 empty] | Subtotal=> | 0.0025582 |  |  |  |  | Subtotal=> | 0.0051305 |  |  |  |  | Subtotal=> | 0.0029431 |  |  |  |  | Subtotal=> | 0.0029431 | 0.013575
0.3
[17 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 3.1 |  |  |  |  | 0.6 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 0.6 |  |  |  |  | 0.1435 | 0.1525 | 0.6 | 0 |  | 0.00062133 | 0.1435 | 0.1525 | 0.5 | 0 |  | 0.00051777 | 0.1435 | 0.1525 | 0.5 | 0 |  | 0.00051777 | 0.1435 | 0.1525 | 0.6 | 0 |  | 0.00062133
[12 empty] | 0.6 |  |  |  |  | 0.105 | 0.1435 | 0.6 | 0.6 |  | 0.0045085 | 0.105 | 0.1435 | 0.5 | 0.5 |  | 0.0037571 | 0.105 | 0.1435 | 0.6 | 0.5 |  | 0.0041134 | 0.105 | 0.1435 | 0.6 | 0.6 |  | 0.0045085
[12 empty] | 0.6 |  |  |  |  | 0.07 | 0.105 | 0.6 | 0.6 |  | 0.0028863 | 0.07 | 0.105 | 0.6 | 0.5 |  | 0.0026298 | 0.07 | 0.105 | 0.6 | 0.6 |  | 0.0028863 | 0.07 | 0.105 | 0.7 | 0.6 |  | 0.0031108
[8 empty] | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.035 | 0.07 | 0.6 | 0.6 |  | 0.0017318 | 0.035 | 0.07 | 0.6 | 0.6 |  | 0.0017318 | 0.035 | 0.07 | 0.6 | 0.6 |  | 0.0017318 | 0.035 | 0.07 | 0.7 | 0.7 |  | 0.0020204
[12 empty] | 0.6 |  |  |  |  | 0 | 0.035 | 0.7 | 0.6 |  | 0.00060934 | 0 | 0.035 | 0.7 | 0.6 |  | 0.00060934 | 0 | 0.035 | 0.7 | 0.6 |  | 0.00060934 | 0 | 0.035 | 0.7 | 0.7 |  | 0.00067348
0.6
[12 empty] | 0.5 | [8 empty] | Subtotal=> | 0.010357 |  |  |  |  | Subtotal=> | 0.0092457 |  |  |  |  | Subtotal=> | 0.0098586 |  |  |  |  | Subtotal=> | 0.010935 | 0.040396
0.5
[17 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 7.2 |  |  |  |  | 0.7 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 0.8 |  |  |  |  | 0.1435 | 0.1525 | 0.7 | 0 |  | 0.00072488 | 0.1435 | 0.1525 | 0.8 | 0 |  | 0.00082844 | 0.1435 | 0.1525 | 0.7 | 0 |  | 0.00072488 | 0.1435 | 0.1525 | 0.8 | 0 |  | 0.00082844
[12 empty] | 1 |  |  |  |  | 0.105 | 0.1435 | 0.8 | 0.7 |  | 0.0056162 | 0.105 | 0.1435 | 0.9 | 0.8 |  | 0.0063676 | 0.105 | 0.1435 | 0.8 | 0.7 |  | 0.0056162 | 0.105 | 0.1435 | 0.8 | 0.8 |  | 0.0060113
[12 empty] | 0.9 |  |  |  |  | 0.07 | 0.105 | 1 | 0.8 |  | 0.0042974 | 0.07 | 0.105 | 0.9 | 0.9 |  | 0.0043295 | 0.07 | 0.105 | 0.9 | 0.8 |  | 0.0040729 | 0.07 | 0.105 | 0.8 | 0.8 |  | 0.0038485
[8 empty] | 0.7 | 0.8 | 0.9 | 1 | 1 | 0.9 | 0.8 | 0.8 | 0.8 | 0.035 | 0.07 | 0.9 | 1 |  | 0.0027581 | 0.035 | 0.07 | 1 | 0.9 |  | 0.002726 | 0.035 | 0.07 | 1 | 0.9 |  | 0.002726 | 0.035 | 0.07 | 0.9 | 0.8 |  | 0.0024374
[12 empty] | 1 |  |  |  |  | 0 | 0.035 | 1 | 0.9 |  | 0.00089797 | 0 | 0.035 | 1 | 1 |  | 0.00096211 | 0 | 0.035 | 1 | 1 |  | 0.00096211 | 0 | 0.035 | 1 | 0.9 |  | 0.00089797
0.9
[12 empty] | 0.9 | [8 empty] | Subtotal=> | 0.014295 |  |  |  |  | Subtotal=> | 0.015214 |  |  |  |  | Subtotal=> | 0.014102 |  |  |  |  | Subtotal=> | 0.014023 | 0.057634
0.8
[17 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 13 |  |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 1.3 |  |  |  |  | 0.1435 | 0.1525 | 1 | 0 |  | 0.0010355 | 0.1435 | 0.1525 | 1.3 | 0 |  | 0.0013462 | 0.1435 | 0.1525 | 1.1 | 0 |  | 0.0011391 | 0.1435 | 0.1525 | 1 | 0 |  | 0.0010355
[12 empty] | 1.4 |  |  |  |  | 0.105 | 0.1435 | 1.3 | 1 |  | 0.008583 | 0.105 | 0.1435 | 1.4 | 1.3 |  | 0.010125 | 0.105 | 0.1435 | 1.3 | 1.1 |  | 0.0089781 | 0.105 | 0.1435 | 1.1 | 1 |  | 0.0078704
[12 empty] | 1.4 |  |  |  |  | 0.07 | 0.105 | 1.4 | 1.3 |  | 0.0064782 | 0.07 | 0.105 | 1.4 | 1.4 |  | 0.0067348 | 0.07 | 0.105 | 1.5 | 1.3 |  | 0.0067027 | 0.07 | 0.105 | 1.2 | 1.1 |  | 0.0055161
[8 empty] | 1.1 | 1.3 | 1.5 | 1.4 | 1.4 | 1.3 | 1.2 | 1.1 | 1 | 0.035 | 0.07 | 1.4 | 1.4 |  | 0.0040409 | 0.035 | 0.07 | 1.5 | 1.4 |  | 0.0041692 | 0.035 | 0.07 | 1.4 | 1.5 |  | 0.0042012 | 0.035 | 0.07 | 1.3 | 1.2 |  | 0.0035919
[12 empty] | 1.5 |  |  |  |  | 0 | 0.035 | 1.4 | 1.4 |  | 0.001347 | 0 | 0.035 | 1.4 | 1.5 |  | 0.0014111 | 0 | 0.035 | 1.4 | 1.4 |  | 0.001347 | 0 | 0.035 | 1.4 | 1.3 |  | 0.0012828
1.4
[12 empty] | 1.4 | [8 empty] | Subtotal=> | 0.021485 |  |  |  |  | Subtotal=> | 0.023786 |  |  |  |  | Subtotal=> | 0.022368 |  |  |  |  | Subtotal=> | 0.019297 | 0.086935
1.3
[17 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 19.7 |  |  |  |  | 1.1 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 1.4 |  |  |  |  | 0.1435 | 0.1525 | 1.1 | 0 |  | 0.0011391 | 0.1435 | 0.1525 | 1.8 | 0 |  | 0.001864 | 0.1435 | 0.1525 | 1.4 | 0 |  | 0.0014498 | 0.1435 | 0.1525 | 1.5 | 0 |  | 0.0015533
[12 empty] | 1.4 |  |  |  |  | 0.105 | 0.1435 | 1.4 | 1.1 |  | 0.0093344 | 0.105 | 0.1435 | 1.8 | 1.8 |  | 0.013525 | 0.105 | 0.1435 | 1.7 | 1.4 |  | 0.011589 | 0.105 | 0.1435 | 1.7 | 1.5 |  | 0.011984
[12 empty] | 1.5 |  |  |  |  | 0.07 | 0.105 | 1.4 | 1.4 |  | 0.0067348 | 0.07 | 0.105 | 2.1 | 1.8 |  | 0.0093325 | 0.07 | 0.105 | 1.8 | 1.7 |  | 0.0084025 | 0.07 | 0.105 | 1.9 | 1.7 |  | 0.0086269
[8 empty] | 1.4 | 1.7 | 1.8 | 2 | 1.9 | 1.9 | 1.9 | 1.7 | 1.5 | 0.035 | 0.07 | 1.5 | 1.4 |  | 0.0041692 | 0.035 | 0.07 | 2 | 2.1 |  | 0.005933 | 0.035 | 0.07 | 2 | 1.8 |  | 0.005452 | 0.035 | 0.07 | 1.9 | 1.9 |  | 0.005484
[12 empty] | 2 |  |  |  |  | 0 | 0.035 | 1.9 | 1.5 |  | 0.0015715 | 0 | 0.035 | 1.9 | 2 |  | 0.0018922 | 0 | 0.035 | 1.9 | 2 |  | 0.0018922 | 0 | 0.035 | 1.9 | 1.9 |  | 0.001828
2.1
[12 empty] | 1.8 | [8 empty] | Subtotal=> | 0.022949 |  |  |  |  | Subtotal=> | 0.032547 |  |  |  |  | Subtotal=> | 0.028785 |  |  |  |  | Subtotal=> | 0.029476 | 0.11376
1.8
[17 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 40.9 |  |  |  |  | 3.4 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 3.7 |  |  |  |  | 0.1435 | 0.1525 | 3.4 | 0 |  | 0.0035209 | 0.1435 | 0.1525 | 2.7 | 0 |  | 0.002796 | 0.1435 | 0.1525 | 3.3 | 0 |  | 0.0034173 | 0.1435 | 0.1525 | 4.3 | 0 |  | 0.0044529
[12 empty] | 3.3 |  |  |  |  | 0.105 | 0.1435 | 3.7 | 3.4 |  | 0.026617 | 0.105 | 0.1435 | 2.6 | 2.7 |  | 0.019932 | 0.105 | 0.1435 | 2.4 | 3.3 |  | 0.02159 | 0.105 | 0.1435 | 4.6 | 4.3 |  | 0.03338
[12 empty] | 2.9 |  |  |  |  | 0.07 | 0.105 | 3.3 | 3.7 |  | 0.016901 | 0.07 | 0.105 | 2.6 | 2.6 |  | 0.012507 | 0.07 | 0.105 | 2.5 | 2.4 |  | 0.01177 | 0.07 | 0.105 | 4.4 | 4.6 |  | 0.02168
[8 empty] | 3.3 | 2.4 | 2.5 | 2.8 | 3.1 | 3.5 | 4.4 | 4.6 | 4.3 | 0.035 | 0.07 | 2.9 | 3.3 |  | 0.0090118 | 0.035 | 0.07 | 2.9 | 2.6 |  | 0.0078893 | 0.035 | 0.07 | 2.8 | 2.5 |  | 0.0076007 | 0.035 | 0.07 | 3.5 | 4.4 |  | 0.011545
[12 empty] | 2.9 |  |  |  |  | 0 | 0.035 | 3.1 | 2.9 |  | 0.0028543 | 0 | 0.035 | 3.1 | 2.9 |  | 0.0028543 | 0 | 0.035 | 3.1 | 2.8 |  | 0.0027901 | 0 | 0.035 | 3.1 | 3.5 |  | 0.0032391
2.6
[12 empty] | 2.6 | [8 empty] | Subtotal=> | 0.058905 |  |  |  |  | Subtotal=> | 0.045979 |  |  |  |  | Subtotal=> | 0.047168 |  |  |  |  | Subtotal=> | 0.074296 | 0.22635
2.7

## Test DC Leakage data
Collated results of cube leakage tests (see raw data starting in cell F4) | [11 empty] | Upper sector | [5 empty] | Lower sector | [5 empty] | Left hand sector | [5 empty] | Right hand sector
ΔpCH | Flow rate (m3.s-1) | [10 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
2.6 | 0 | Calculations to convert speed measurements to flow rates start in cell Y1
9.4 | 0.002608 | ΔpCH | Air speed measurements within supply air duct (m/s)
12 | 0.007995 | 2.6 |  |  |  |  | 0
19.8 | 0.014992 | [5 empty] | 0 |  |  |  |  | 0.1435 | 0.1525 | 0 | 0 |  | 0 | 0.1435 | 0.1525 | 0 | 0 |  | 0 | 0.1435 | 0.1525 | 0 | 0 |  | 0 | 0.1435 | 0.1525 | 0 | 0 |  | 0
27.2 | 0.019995 | [5 empty] | 0 |  |  |  |  | 0.105 | 0.1435 | 0 | 0 |  | 0 | 0.105 | 0.1435 | 0 | 0 |  | 0 | 0.105 | 0.1435 | 0 | 0 |  | 0 | 0.105 | 0.1435 | 0 | 0 |  | 0
39.9 | 0.028488 | [5 empty] | 0 |  |  |  |  | 0.07 | 0.105 | 0 | 0 |  | 0 | 0.07 | 0.105 | 0 | 0 |  | 0 | 0.07 | 0.105 | 0 | 0 |  | 0 | 0.07 | 0.105 | 0 | 0 |  | 0
51.8 | 0.037174 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035 | 0.07 | 0 | 0 |  | 0 | 0.035 | 0.07 | 0 | 0 |  | 0 | 0.035 | 0.07 | 0 | 0 |  | 0 | 0.035 | 0.07 | 0 | 0 |  | 0
[7 empty] | 0 |  |  |  |  | 0 | 0.035 | 0 | 0 |  | 0 | 0 | 0.035 | 0 | 0 |  | 0 | 0 | 0.035 | 0 | 0 |  | 0 | 0 | 0.035 | 0 | 0 |  | 0
Interpolating the above results, to estimate the leakage at the pressures at which measurements were taken for the bypass in the test data centre. This is then halved, since only have of the cube is pressurised during the bypass tests, whereas the entire cube was pressurised during the cube leakage tests. | [6 empty] | 0
ΔpCH | Flow rate (m3.s-1) | [5 empty] | 0 | [8 empty] | Subtotal=> | 0 |  |  |  |  | Subtotal=> | 0 |  |  |  |  | Subtotal=> | 0 |  |  |  |  | Subtotal=> | 0 | 0
1.1 | 0 | [5 empty] | 0
3.1 | 9.5882e-05
7.2 | 0.00088212 | [10 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
13 | 0.004446 | [10 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
19.7 | 0.0074511 | [10 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #REF! |  |  | 0 | 0 | 0 | 0
|  | 9.4 |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 0 |  |  |  |  | 0.1435 | 0.1525 | 0 | 0 |  | 0 | 0.1435 | 0.1525 | 0.1 | 0 |  | 0.00010355 | 0.1435 | 0.1525 | 0.1 | 0 |  | 0.00010355 | 0.1435 | 0.1525 | 0 | 0 |  | 0
[7 empty] | 0 |  |  |  |  | 0.105 | 0.1435 | 0 | 0 |  | 0 | 0.105 | 0.1435 | 0.1 | 0.1 |  | 0.00075141 | 0.105 | 0.1435 | 0.1 | 0.1 |  | 0.00075141 | 0.105 | 0.1435 | 0 | 0 |  | 0
[7 empty] | 0 |  |  |  |  | 0.07 | 0.105 | 0 | 0 |  | 0 | 0.07 | 0.105 | 0 | 0.1 |  | 0.00025656 | 0.07 | 0.105 | 0.1 | 0.1 |  | 0.00048106 | 0.07 | 0.105 | 0 | 0 |  | 0
|  |  | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.035 | 0.07 | 0 | 0 |  | 0 | 0.035 | 0.07 | 0 | 0 |  | 0 | 0.035 | 0.07 | 0 | 0.1 |  | 0.00016035 | 0.035 | 0.07 | 0 | 0 |  | 0
[7 empty] | 0 |  |  |  |  | 0 | 0.035 | 0 | 0 |  | 0 | 0 | 0.035 | 0 | 0 |  | 0 | 0 | 0.035 | 0 | 0 |  | 0 | 0 | 0.035 | 0 | 0 |  | 0
0
[7 empty] | 0.1 | [8 empty] | Subtotal=> | 0 |  |  |  |  | Subtotal=> | 0.0011115 |  |  |  |  | Subtotal=> | 0.0014964 |  |  |  |  | Subtotal=> | 0 | 0.0026079
0.1
[12 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #REF! |  |  | 0 | 0 | 0 | 0
|  | 12 |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 0.1 |  |  |  |  | 0.1435 | 0.1525 | 0 | 0 |  | 0 | 0.1435 | 0.1525 | 0.2 | 0 |  | 0.00020711 | 0.1435 | 0.1525 | 0.2 | 0 |  | 0.00020711 | 0.1435 | 0.1525 | 0.1 | 0 |  | 0.00010355
[7 empty] | 0.1 |  |  |  |  | 0.105 | 0.1435 | 0.1 | 0 |  | 0.0003563 | 0.105 | 0.1435 | 0.1 | 0.2 |  | 0.0011465 | 0.105 | 0.1435 | 0.2 | 0.2 |  | 0.0015028 | 0.105 | 0.1435 | 0.1 | 0.1 |  | 0.00075141
[7 empty] | 0.1 |  |  |  |  | 0.07 | 0.105 | 0.1 | 0.1 |  | 0.00048106 | 0.07 | 0.105 | 0.1 | 0.1 |  | 0.00048106 | 0.07 | 0.105 | 0.2 | 0.2 |  | 0.00096211 | 0.07 | 0.105 | 0 | 0.1 |  | 0.00025656
|  |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 0.1 | 0.1 | 0.035 | 0.07 | 0.1 | 0.1 |  | 0.00028863 | 0.035 | 0.07 | 0.1 | 0.1 |  | 0.00028863 | 0.035 | 0.07 | 0.2 | 0.2 |  | 0.00057727 | 0.035 | 0.07 | 0 | 0 |  | 0
[7 empty] | 0.1 |  |  |  |  | 0 | 0.035 | 0.1 | 0.1 |  | 9.6211e-05 | 0 | 0.035 | 0.1 | 0.1 |  | 9.6211e-05 | 0 | 0.035 | 0.1 | 0.2 |  | 0.00016035 | 0 | 0.035 | 0.1 | 0 |  | 3.207e-05
0.1
[7 empty] | 0.1 | [8 empty] | Subtotal=> | 0.0012222 |  |  |  |  | Subtotal=> | 0.0022195 |  |  |  |  | Subtotal=> | 0.0034097 |  |  |  |  | Subtotal=> | 0.0011436 | 0.007995
0.2
[12 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #REF! |  |  | 0 | 0 | 0 | 0
|  | 19.8 |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 0.1 |  |  |  |  | 0.1435 | 0.1525 | 0 | 0 |  | 0 | 0.1435 | 0.1525 | 0.3 | 0 |  | 0.00031066 | 0.1435 | 0.1525 | 0.3 | 0 |  | 0.00031066 | 0.1435 | 0.1525 | 0.4 | 0 |  | 0.00041422
[7 empty] | 0.1 |  |  |  |  | 0.105 | 0.1435 | 0.1 | 0 |  | 0.0003563 | 0.105 | 0.1435 | 0.3 | 0.3 |  | 0.0022542 | 0.105 | 0.1435 | 0.3 | 0.3 |  | 0.0022542 | 0.105 | 0.1435 | 0.2 | 0.4 |  | 0.002293
[7 empty] | 0.2 |  |  |  |  | 0.07 | 0.105 | 0.1 | 0.1 |  | 0.00048106 | 0.07 | 0.105 | 0.3 | 0.3 |  | 0.0014432 | 0.07 | 0.105 | 0.3 | 0.3 |  | 0.0014432 | 0.07 | 0.105 | 0 | 0.2 |  | 0.00051313
|  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.1 | 0 | 0.2 | 0.4 | 0.035 | 0.07 | 0.2 | 0.1 |  | 0.00041692 | 0.035 | 0.07 | 0.2 | 0.3 |  | 0.00073762 | 0.035 | 0.07 | 0.3 | 0.3 |  | 0.0008659 | 0.035 | 0.07 | 0.1 | 0 |  | 0.00012828
[7 empty] | 0.2 |  |  |  |  | 0 | 0.035 | 0.2 | 0.2 |  | 0.00019242 | 0 | 0.035 | 0.2 | 0.2 |  | 0.00019242 | 0 | 0.035 | 0.2 | 0.3 |  | 0.00025656 | 0 | 0.035 | 0.2 | 0.1 |  | 0.00012828
0.3
[7 empty] | 0.3 | [8 empty] | Subtotal=> | 0.0014467 |  |  |  |  | Subtotal=> | 0.0049381 |  |  |  |  | Subtotal=> | 0.0051305 |  |  |  |  | Subtotal=> | 0.0034769 | 0.014992
0.3
[12 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #REF! |  |  | 0 | 0 | 0 | 0
|  | 27.2 |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 0.1 |  |  |  |  | 0.1435 | 0.1525 | 0 | 0 |  | 0 | 0.1435 | 0.1525 | 0.4 | 0 |  | 0.00041422 | 0.1435 | 0.1525 | 0.4 | 0 |  | 0.00041422 | 0.1435 | 0.1525 | 0.5 | 0 |  | 0.00051777
[7 empty] | 0.1 |  |  |  |  | 0.105 | 0.1435 | 0.1 | 0 |  | 0.0003563 | 0.105 | 0.1435 | 0.4 | 0.4 |  | 0.0030056 | 0.105 | 0.1435 | 0.4 | 0.4 |  | 0.0030056 | 0.105 | 0.1435 | 0.3 | 0.5 |  | 0.0030444
[7 empty] | 0.2 |  |  |  |  | 0.07 | 0.105 | 0.1 | 0.1 |  | 0.00048106 | 0.07 | 0.105 | 0.4 | 0.4 |  | 0.0019242 | 0.07 | 0.105 | 0.4 | 0.4 |  | 0.0019242 | 0.07 | 0.105 | 0 | 0.3 |  | 0.00076969
|  |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.2 | 0 | 0.3 | 0.5 | 0.035 | 0.07 | 0.2 | 0.1 |  | 0.00041692 | 0.035 | 0.07 | 0.4 | 0.4 |  | 0.0011545 | 0.035 | 0.07 | 0.4 | 0.4 |  | 0.0011545 | 0.035 | 0.07 | 0.2 | 0 |  | 0.00025656
[7 empty] | 0.4 |  |  |  |  | 0 | 0.035 | 0.3 | 0.2 |  | 0.00022449 | 0 | 0.035 | 0.3 | 0.4 |  | 0.00035277 | 0 | 0.035 | 0.3 | 0.4 |  | 0.00035277 | 0 | 0.035 | 0.3 | 0.2 |  | 0.00022449
0.4
[7 empty] | 0.4 | [8 empty] | Subtotal=> | 0.0014788 |  |  |  |  | Subtotal=> | 0.0068514 |  |  |  |  | Subtotal=> | 0.0068514 |  |  |  |  | Subtotal=> | 0.004813 | 0.019995
0.4
[12 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #REF! |  |  | 0 | 0 | 0 | 0
|  | 39.9 |  |  |  |  | 0.4 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 0.4 |  |  |  |  | 0.1435 | 0.1525 | 0.4 | 0 |  | 0.00041422 | 0.1435 | 0.1525 | 0.5 | 0 |  | 0.00051777 | 0.1435 | 0.1525 | 0.5 | 0 |  | 0.00051777 | 0.1435 | 0.1525 | 0.5 | 0 |  | 0.00051777
[7 empty] | 0.3 |  |  |  |  | 0.105 | 0.1435 | 0.4 | 0.4 |  | 0.0030056 | 0.105 | 0.1435 | 0.5 | 0.5 |  | 0.0037571 | 0.105 | 0.1435 | 0.5 | 0.5 |  | 0.0037571 | 0.105 | 0.1435 | 0.3 | 0.5 |  | 0.0030444
[7 empty] | 0.4 |  |  |  |  | 0.07 | 0.105 | 0.3 | 0.4 |  | 0.0016997 | 0.07 | 0.105 | 0.5 | 0.5 |  | 0.0024053 | 0.07 | 0.105 | 0.5 | 0.5 |  | 0.0024053 | 0.07 | 0.105 | 0 | 0.3 |  | 0.00076969
|  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.2 | 0 | 0.3 | 0.5 | 0.035 | 0.07 | 0.4 | 0.3 |  | 0.00099418 | 0.035 | 0.07 | 0.5 | 0.5 |  | 0.0014432 | 0.035 | 0.07 | 0.5 | 0.5 |  | 0.0014432 | 0.035 | 0.07 | 0.2 | 0 |  | 0.00025656
[7 empty] | 0.5 |  |  |  |  | 0 | 0.035 | 0.4 | 0.4 |  | 0.00038485 | 0 | 0.035 | 0.4 | 0.5 |  | 0.00044899 | 0 | 0.035 | 0.4 | 0.5 |  | 0.00044899 | 0 | 0.035 | 0.4 | 0.2 |  | 0.00025656
0.5
[7 empty] | 0.5 | [8 empty] | Subtotal=> | 0.0064986 |  |  |  |  | Subtotal=> | 0.0085723 |  |  |  |  | Subtotal=> | 0.0085723 |  |  |  |  | Subtotal=> | 0.004845 | 0.028488
0.5
[12 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | #REF! | 0 |  |  | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #REF! |  |  | 0 | 0 | 0 | 0
|  | 51.8 |  |  |  |  | 0.6 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[7 empty] | 0.5 |  |  |  |  | 0.1435 | 0.1525 | 0.6 | 0 |  | 0.00062133 | 0.1435 | 0.1525 | 0.6 | 0 |  | 0.00062133 | 0.1435 | 0.1525 | 0.6 | 0 |  | 0.00062133 | 0.1435 | 0.1525 | 0.7 | 0 |  | 0.00072488
[7 empty] | 0.4 |  |  |  |  | 0.105 | 0.1435 | 0.5 | 0.6 |  | 0.0041522 | 0.105 | 0.1435 | 0.6 | 0.6 |  | 0.0045085 | 0.105 | 0.1435 | 0.6 | 0.6 |  | 0.0045085 | 0.105 | 0.1435 | 0.5 | 0.7 |  | 0.0045473
[7 empty] | 0.5 |  |  |  |  | 0.07 | 0.105 | 0.4 | 0.5 |  | 0.0021808 | 0.07 | 0.105 | 0.6 | 0.6 |  | 0.0028863 | 0.07 | 0.105 | 0.6 | 0.6 |  | 0.0028863 | 0.07 | 0.105 | 0.1 | 0.5 |  | 0.0015073
|  |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.4 | 0.1 | 0.5 | 0.7 | 0.035 | 0.07 | 0.5 | 0.4 |  | 0.0012828 | 0.035 | 0.07 | 0.6 | 0.6 |  | 0.0017318 | 0.035 | 0.07 | 0.6 | 0.6 |  | 0.0017318 | 0.035 | 0.07 | 0.4 | 0.1 |  | 0.00067348
[7 empty] | 0.6 |  |  |  |  | 0 | 0.035 | 0.5 | 0.5 |  | 0.00048106 | 0 | 0.035 | 0.5 | 0.6 |  | 0.0005452 | 0 | 0.035 | 0.5 | 0.6 |  | 0.0005452 | 0 | 0.035 | 0.5 | 0.4 |  | 0.00041692
0.6
[7 empty] | 0.6 | [8 empty] | Subtotal=> | 0.0087181 |  |  |  |  | Subtotal=> | 0.010293 |  |  |  |  | Subtotal=> | 0.010293 |  |  |  |  | Subtotal=> | 0.0078699 | 0.037174
0.6

## Repeat readings
Single rack tests (note that the tests which were repeated are not the same tests for which results were reported in the paper, however, the same methods were used)
Test A
Original test |  |  | Repeat test |  |  | Original data interpolated
ΔpCH (Pa) | Measured speed (m.s-1) |  | ΔpCH (Pa) | Measured speed (m.s-1) |  | ΔpCH (Pa) | Interpolated speed (m.s-1) | % Difference | Absolute % difference
4 | 0.6 |  | 4 | 0.65 |  | 4 | 0.6 | -8.3333 | 8.3333
5.5 | 0.7 |  | 6 | 0.7 |  | 6 | 0.72778 | 3.8168 | 3.8168
10 | 0.95 |  | 13 | 1.1 |  | 13 | 1.0786 | -1.9868 | 1.9868
17 | 1.25 |  | 20 | 1.3 |  | 20 | 1.425 | 8.7719 | 8.7719
23 | 1.6 |  | 31 | 1.7 |  | 31 | 1.7655 | 3.7109 | 3.7109
37.5 | 1.9 |  | 51 | 2.4 |  | 51 | 2.5 | 4 | 4
51 | 2.5 |  | 69 | 2.9 |  | 69 | 2.9516 | 1.7486 | 1.7486
67 | 2.9 |  | 84 | 3.5 |  | 84 | 3.3585 | -4.2121 | 4.2121
82.5 | 3.3 |  | 103 | 4.1 |  | 103 | 4.1 | 0 | 0
103 | 4.1
Test B
Original test |  |  | Repeat test |  |  | Original data interpolated
ΔpCH (Pa) | Measured speed (m.s-1) |  | ΔpCH (Pa) | Measured speed (m.s-1) |  | ΔpCH (Pa) | Interpolated speed (m.s-1) | % Difference | Absolute % difference
4 | 0.3 |  | 3.5 | 0.3 |  | 3.5 | 0.2625 | -14.2857 | 14.2857
7 | 0.4 |  | 4.5 | 0.4 |  | 4.5 | 0.31667 | -26.3158 | 26.3158
9 | 0.6 |  | 9 | 0.6 |  | 9 | 0.6 | 0 | 0
16 | 0.8 |  | 14 | 0.8 |  | 14 | 0.74286 | -7.6923 | 7.6923
29 | 1.2 |  | 21 | 1 |  | 21 | 0.95385 | -4.8387 | 4.8387
46 | 1.7 |  | 36 | 1.5 |  | 36 | 1.4059 | -6.6946 | 6.6946
61 | 2.2 |  | 52 | 2 |  | 52 | 1.9 | -5.2632 | 5.2632
83 | 2.8 |  | 73 | 2.7 |  | 73 | 2.5273 | -6.8345 | 6.8345
102 | 3.3 |  | 91 | 3.1 |  | 91 | 3.0105 | -2.972 | 2.972
|  |  | 100 | 3.5 |  | 100 | 3.2474 | -7.7796 | 7.7796
Test C
Original test |  |  | Repeat test |  |  | Original data interpolated
ΔpCH (Pa) | Measured speed (m.s-1) |  | ΔpCH (Pa) | Measured speed (m.s-1) |  | ΔpCH (Pa) | Interpolated speed (m.s-1) | % Difference | Absolute % difference
4 | 0.45 |  | 3 | 0.55 |  | 3 | 0.3375 | -62.963 | 62.963
6 | 0.55 |  | 6 | 0.7 |  | 6 | 0.55 | -27.2727 | 27.2727
9.5 | 0.75 |  | 10 | 0.9 |  | 10 | 0.8 | -12.5 | 12.5
11.5 | 0.95 |  | 16 | 1.15 |  | 16 | 1.025 | -12.1951 | 12.1951
23.5 | 1.15 |  | 26 | 1.4 |  | 26 | 1.2235 | -14.4231 | 14.4231
32 | 1.4 |  | 40 | 1.7 |  | 40 | 1.5778 | -7.7465 | 7.7465
41 | 1.6 |  | 55 | 2.2 |  | 55 | 2.0059 | -9.6774 | 9.6774
52 | 1.9 |  | 72 | 2.8 |  | 72 | 2.56 | -9.375 | 9.375
69 | 2.5 |  | 90 | 3.2 |  | 90 | 2.9895 | -7.0423 | 7.0423
84 | 2.8 |  | 100 | 3.7 |  | 100 | 3.3053 | -11.9427 | 11.9427
103 | 3.4
[8 empty] | RMS % Difference => | 10.1515
[18 empty] | Upper sector | [5 empty] | Lower sector | [5 empty] | Left hand sector | [5 empty] | Right hand sector
[18 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Total flow rate (m3.s-1)
Test data centre | [7 empty] | Calculations to convert speed measurements to flow rates start in cell AB46 | [9 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | -15.9791 | 0 |  |  | 0 | 0 | 0 | 0
Repeat readings (see speed measurements starting at cell I49) |  | Original data |  | Original data interpolated |  |  |  | ΔpCH | Air Speed Measurements | [8 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | -15.9791 |  |  | 0 | 0 | 0 | 0
ΔpCH (Pa) | Measured flow rate (m3.s-1) | ΔpCH (Pa) | Measured flow rate (m3.s-1) | ΔpCH (Pa) | Flow rate (m3.s-1) | % Difference |  | 9.7 |  |  |  |  | 0.8 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5.5 | 0.048876 | 1.1 | 0.013575 | 5.5 | 0.050486 | 3.1904 | [6 empty] | 0.8 |  |  |  |  | 0.1435 | 0.1525 | 0.8 | 0 |  | 0.00082844 | 0.1435 | 0.1525 | 1.2 | 0 |  | 0.0012427 | 0.1435 | 0.1525 | 0.9 | 0 |  | 0.00093199 | 0.1435 | 0.1525 | 1.1 | 0 |  | 0.0011391
9.7 | 0.069825 | 3.1 | 0.040396 | 9.7 | 0.070264 | 0.62401 | [6 empty] | 0.9 |  |  |  |  | 0.105 | 0.1435 | 0.8 | 0.8 |  | 0.0060113 | 0.105 | 0.1435 | 1.1 | 1.2 |  | 0.0086606 | 0.105 | 0.1435 | 1 | 0.9 |  | 0.007119 | 0.105 | 0.1435 | 1 | 1.1 |  | 0.0079092
12.2 | 0.080813 | 7.2 | 0.057634 | 12.2 | 0.082894 | 2.5097 | [6 empty] | 0.9 |  |  |  |  | 0.07 | 0.105 | 0.9 | 0.8 |  | 0.0040729 | 0.07 | 0.105 | 1.1 | 1.1 |  | 0.0052916 | 0.07 | 0.105 | 1.1 | 1 |  | 0.0050351 | 0.07 | 0.105 | 1.1 | 1 |  | 0.0050351
22.5 | 0.15155 | 13 | 0.086935 | 22.5 | 0.13067 | -15.9791 |  |  | 0.9 | 1 | 1.1 | 1.2 | 1.2 | 1.1 | 1.1 | 1 | 1.1 | 0.035 | 0.07 | 0.9 | 0.9 |  | 0.0025977 | 0.035 | 0.07 | 1.1 | 1.1 |  | 0.003175 | 0.035 | 0.07 | 1.2 | 1.1 |  | 0.0033033 | 0.035 | 0.07 | 1.1 | 1.1 |  | 0.003175
|  | 19.7 | 0.11376 |  | RMS % Difference => | 5.5758 | [6 empty] | 1.1 |  |  |  |  | 0 | 0.035 | 1.2 | 0.9 |  | 0.00096211 | 0 | 0.035 | 1.2 | 1.1 |  | 0.0010904 | 0 | 0.035 | 1.2 | 1.2 |  | 0.0011545 | 0 | 0.035 | 1.2 | 1.1 |  | 0.0010904
|  | 30.5 | 0.17899 | [9 empty] | 1.1
[13 empty] | 1.1 | [8 empty] | Subtotal=> | 0.014472 |  |  |  |  | Subtotal=> | 0.01946 |  |  |  |  | Subtotal=> | 0.017544 |  |  |  |  | Subtotal=> | 0.018349 | 0.069825
1.2
[18 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s)
[18 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[8 empty] | 22.5 |  |  |  |  | 2.1 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[13 empty] | 2.3 |  |  |  |  | 0.1435 | 0.1525 | 2.1 | 0 |  | 0.0021746 | 0.1435 | 0.1525 | 2.3 | 0 |  | 0.0023818 | 0.1435 | 0.1525 | 1.2 | 0 |  | 0.0012427 | 0.1435 | 0.1525 | 3.1 | 0 |  | 0.0032102
[13 empty] | 2 |  |  |  |  | 0.105 | 0.1435 | 2.3 | 2.1 |  | 0.016492 | 0.105 | 0.1435 | 2 | 2.3 |  | 0.016214 | 0.105 | 0.1435 | 1.2 | 1.2 |  | 0.0090169 | 0.105 | 0.1435 | 3.4 | 3.1 |  | 0.024363
[13 empty] | 1.9 |  |  |  |  | 0.07 | 0.105 | 2 | 2.3 |  | 0.010391 | 0.07 | 0.105 | 2 | 2 |  | 0.0096211 | 0.07 | 0.105 | 1.5 | 1.2 |  | 0.0064462 | 0.07 | 0.105 | 3.4 | 3.4 |  | 0.016356
[9 empty] | 1.2 | 1.2 | 1.5 | 1.9 | 1.9 | 3 | 3.4 | 3.4 | 3.1 | 0.035 | 0.07 | 1.9 | 2 |  | 0.0056444 | 0.035 | 0.07 | 2 | 2 |  | 0.0057727 | 0.035 | 0.07 | 1.9 | 1.5 |  | 0.0048426 | 0.035 | 0.07 | 3 | 3.4 |  | 0.0093004
[13 empty] | 2 |  |  |  |  | 0 | 0.035 | 1.9 | 1.9 |  | 0.001828 | 0 | 0.035 | 1.9 | 2 |  | 0.0018922 | 0 | 0.035 | 1.9 | 1.9 |  | 0.001828 | 0 | 0.035 | 1.9 | 3 |  | 0.0025336
2
[13 empty] | 2 | [8 empty] | Subtotal=> | 0.03653 |  |  |  |  | Subtotal=> | 0.035881 |  |  |  |  | Subtotal=> | 0.023376 |  |  |  |  | Subtotal=> | 0.055763 | 0.15155
2.3
[18 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s)
[18 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[8 empty] | 5.5 |  |  |  |  | 0.5 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[13 empty] | 0.5 |  |  |  |  | 0.1435 | 0.1525 | 0.5 | 0 |  | 0.00051777 | 0.1435 | 0.1525 | 0.7 | 0 |  | 0.00072488 | 0.1435 | 0.1525 | 0.5 | 0 |  | 0.00051777 | 0.1435 | 0.1525 | 1 | 0 |  | 0.0010355
[13 empty] | 0.5 |  |  |  |  | 0.105 | 0.1435 | 0.5 | 0.5 |  | 0.0037571 | 0.105 | 0.1435 | 0.8 | 0.7 |  | 0.0056162 | 0.105 | 0.1435 | 0.6 | 0.5 |  | 0.0041134 | 0.105 | 0.1435 | 1 | 1 |  | 0.0075141
[13 empty] | 0.6 |  |  |  |  | 0.07 | 0.105 | 0.5 | 0.5 |  | 0.0024053 | 0.07 | 0.105 | 0.8 | 0.8 |  | 0.0038485 | 0.07 | 0.105 | 0.6 | 0.6 |  | 0.0028863 | 0.07 | 0.105 | 1 | 1 |  | 0.0048106
[9 empty] | 0.5 | 0.6 | 0.6 | 0.7 | 0.7 | 0.9 | 1 | 1 | 1 | 0.035 | 0.07 | 0.6 | 0.5 |  | 0.0015715 | 0.035 | 0.07 | 0.7 | 0.8 |  | 0.0021808 | 0.035 | 0.07 | 0.7 | 0.6 |  | 0.0018601 | 0.035 | 0.07 | 0.9 | 1 |  | 0.0027581
[13 empty] | 0.7 |  |  |  |  | 0 | 0.035 | 0.7 | 0.6 |  | 0.00060934 | 0 | 0.035 | 0.7 | 0.7 |  | 0.00067348 | 0 | 0.035 | 0.7 | 0.7 |  | 0.00067348 | 0 | 0.035 | 0.7 | 0.9 |  | 0.00080176
0.8
[13 empty] | 0.8 | [8 empty] | Subtotal=> | 0.0088609 |  |  |  |  | Subtotal=> | 0.013044 |  |  |  |  | Subtotal=> | 0.010051 |  |  |  |  | Subtotal=> | 0.01692 | 0.048876
0.7
[18 empty] | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s) | Inner radius of section (m) | Outer radius of section (m) | Speed at inner radius (m/s) | Speed at outer radius (m/s) |  | Flow within section (m3/s)
[18 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[8 empty] | 12.2 |  |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[13 empty] | 0.8 |  |  |  |  | 0.1435 | 0.1525 | 1 | 0 |  | 0.0010355 | 0.1435 | 0.1525 | 1.1 | 0 |  | 0.0011391 | 0.1435 | 0.1525 | 0.6 | 0 |  | 0.00062133 | 0.1435 | 0.1525 | 1.8 | 0 |  | 0.001864
[13 empty] | 0.6 |  |  |  |  | 0.105 | 0.1435 | 0.8 | 1 |  | 0.0068015 | 0.105 | 0.1435 | 1.2 | 1.1 |  | 0.0086218 | 0.105 | 0.1435 | 0.7 | 0.6 |  | 0.0048648 | 0.105 | 0.1435 | 2 | 1.8 |  | 0.014238
[13 empty] | 0.9 |  |  |  |  | 0.07 | 0.105 | 0.6 | 0.8 |  | 0.0033995 | 0.07 | 0.105 | 1.2 | 1.2 |  | 0.0057727 | 0.07 | 0.105 | 0.8 | 0.7 |  | 0.0035919 | 0.07 | 0.105 | 2 | 2 |  | 0.0096211
[9 empty] | 0.6 | 0.7 | 0.8 | 1.3 | 1.3 | 1.9 | 2 | 2 | 1.8 | 0.035 | 0.07 | 0.9 | 0.6 |  | 0.0021166 | 0.035 | 0.07 | 1.2 | 1.2 |  | 0.0034636 | 0.035 | 0.07 | 1.3 | 0.8 |  | 0.0029505 | 0.035 | 0.07 | 1.9 | 2 |  | 0.0056444
[13 empty] | 1.2 |  |  |  |  | 0 | 0.035 | 1.3 | 0.9 |  | 0.00099418 | 0 | 0.035 | 1.3 | 1.2 |  | 0.0011866 | 0 | 0.035 | 1.3 | 1.3 |  | 0.0012507 | 0 | 0.035 | 1.3 | 1.9 |  | 0.0016356
1.2
[13 empty] | 1.2 | [8 empty] | Subtotal=> | 0.014347 |  |  |  |  | Subtotal=> | 0.020184 |  |  |  |  | Subtotal=> | 0.013279 |  |  |  |  | Subtotal=> | 0.033003 | 0.080813
1.1